## Calculator
Generator fuel calculator (engine-family model v3)
Yellow cells are inputs. Fuel per hour = country × rated kW × (a + b×loading + q×loading²). L/kWh = fuel per hour ÷ (rated kW × loading).
Engine family | Cummins KTA50 (1250 kVA)
Country | UAE
Rated kVA | 500
Loading (fraction of rated kW) | 0.35
Family options: Cummins KTA50 (1250 kVA), Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Cummins QSL9 (250–300 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), JCB 448 (125 kVA), JCB 448 (60 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA), Scania DC13 (500 kVA), Volvo TAD1651 (500 kVA), unlisted 200–220 kVA, unlisted 300 kVA, unlisted 500 kVA, unlisted ≤125 kVA
a (fixed, L per rated-kW-hour) | 0.040547
b (marginal, L/kWh) | 0.17976
q (quadratic, L/kWh per unit loading) | 0.078694
Country multiplier | 0.97128
Rated kW (kVA × 0.8) | 400
Fuel at this loading, L/h | 43.9426
L/kWh at this loading | 0.31388
L/kWh at 25% / 50% / 75% | 0.35124 | 0.29158 | 0.28444

## Coefficients
Engine family | Rated kVA (typical) | a fixed (L per rated-kW-h) | b marginal (L/kWh) | site-months in fit | sites in fit | Share of fleet kWh | q, KSA, UAE
Cummins KTA50 (1250 kVA) | 1250 | 0.040547 | 0.17976 | 66 | 8 | 0.3255 | 0.078694 | q (quadratic)
Cummins QSG12 (350 kVA) | 350 | 0.041425 | 0.18516 | 45 | 8 | 0.0198 | 1.0538 | KSA multiplier
Cummins QSK23 (800 kVA) | 800 | 0.03193 | 0.18469 | 75 | 7 | 0.1606 | 0.97128 | UAE multiplier
Cummins QSL9 (250–300 kVA) | 300 | 0.040357 | 0.19691 | 48 | 7 | 0.0161
Cummins QST30 (1000 kVA) | 1000 | 0.018754 | 0.20778 | 69 | 7 | 0.1163
Cummins QSX15 (500 kVA) | 500 | 0.03742 | 0.18977 | 44 | 6 | 0.0455
JCB 448 (125 kVA) | 125 | 0.039877 | 0.23359 | 97 | 10 | 0.0177
JCB 448 (60 kVA) | 60 | 0.0079597 | 0.2716 | 15 | 2 | 0.0008
JD 6068 (220 kVA) | 220 | 0.047306 | 0.25526 | 78 | 9 | 0.0125
JD 6090 (300 kVA) | 300 | 0.042325 | 0.28671 | 101 | 16 | 0.0112
Scania DC13 (500 kVA) | 500 | 0.025915 | 0.16835 | 8 | 1 | 0.0381
Volvo TAD1651 (500 kVA) | 500 | 0.033439 | 0.19947 | 143 | 18 | 0.1675
unlisted 200–220 kVA | 220 | 0 | 0.41548 | 9 | 3 | 0.0022
unlisted 300 kVA | 300 | 0.052485 | 0.1162 | 11 | 2 | 0.0064
unlisted 500 kVA | 500 | 0.045589 | 0.14429 | 34 | 5 | 0.0498
unlisted ≤125 kVA | 125 | 0.027284 | 0.28786 | 17 | 1 | 0.0032
Fitted on 384 site-months (Jan 2025–Sep 2026) from 37 sites: monthly-report fuel vs hourly unit counters, leave-one-site-out tested. Families from the RSS generator list (Oct 2026). "unlisted" = units with no make/model in the list.

## Curves L per kWh
Engine family | Country | 25% | 35% | 50% | 75% | 35% low (p10) | 35% high (p90)
Cummins KTA50 (1250 kVA) | KSA | 0.38108 | 0.34054 | 0.31635 | 0.3086 | 0.329 | 0.351
Cummins KTA50 (1250 kVA) | UAE | 0.35124 | 0.31388 | 0.29158 | 0.28444 | 0.303 | 0.337
Cummins QSG12 (350 kVA) | KSA | 0.39046 | 0.34886 | 0.32389 | 0.31552 | 0.31 | 0.392
Cummins QSG12 (350 kVA) | UAE | 0.35989 | 0.32155 | 0.29853 | 0.29081 | 0.294 | 0.364
Cummins QSK23 (800 kVA) | KSA | 0.34995 | 0.31979 | 0.30339 | 0.30169 | 0.299 | 0.326
Cummins QSK23 (800 kVA) | UAE | 0.32255 | 0.29475 | 0.27963 | 0.27807 | 0.285 | 0.299
Cummins QSL9 (250–300 kVA) | KSA | 0.39835 | 0.35804 | 0.33402 | 0.3264 | 0.34 | 0.371
Cummins QSL9 (250–300 kVA) | UAE | 0.36716 | 0.33 | 0.30787 | 0.30085 | 0.326 | 0.341
Cummins QST30 (1000 kVA) | KSA | 0.31874 | 0.30444 | 0.29994 | 0.3075 | 0.292 | 0.331
Cummins QST30 (1000 kVA) | UAE | 0.29378 | 0.28061 | 0.27646 | 0.28342 | 0.271 | 0.312
Cummins QSX15 (500 kVA) | KSA | 0.37844 | 0.34167 | 0.32031 | 0.31475 | 0.329 | 0.369
Cummins QSX15 (500 kVA) | UAE | 0.34881 | 0.31492 | 0.29523 | 0.29011 | 0.312 | 0.354
JCB 448 (125 kVA) | KSA | 0.43497 | 0.39524 | 0.37166 | 0.36438 | 0.369 | 0.415
JCB 448 (125 kVA) | UAE | 0.40092 | 0.3643 | 0.34256 | 0.33585 | 0.342 | 0.389
JCB 448 (60 kVA) | KSA | 0.34049 | 0.3392 | 0.34445 | 0.35959 | 0.301 | 0.349
JCB 448 (60 kVA) | UAE | 0.31383 | 0.31264 | 0.31748 | 0.33143 | 0.28 | 0.329
JD 6068 (220 kVA) | KSA | 0.48912 | 0.44044 | 0.41015 | 0.39765 | 0.415 | 0.45
JD 6068 (220 kVA) | UAE | 0.45082 | 0.40596 | 0.37804 | 0.36651 | 0.387 | 0.418
JD 6090 (300 kVA) | KSA | 0.50128 | 0.4586 | 0.43281 | 0.4238 | 0.421 | 0.492
JD 6090 (300 kVA) | UAE | 0.46203 | 0.42269 | 0.39892 | 0.39062 | 0.395 | 0.452
Scania DC13 (500 kVA) | KSA | 0.30737 | 0.28446 | 0.27349 | 0.27601 | 0.283 | 0.286
Scania DC13 (500 kVA) | UAE | 0.28331 | 0.26218 | 0.25207 | 0.2544 | 0.26 | 0.276
Volvo TAD1651 (500 kVA) | KSA | 0.37188 | 0.3399 | 0.32214 | 0.31938 | 0.333 | 0.346
Volvo TAD1651 (500 kVA) | UAE | 0.34276 | 0.31329 | 0.29691 | 0.29437 | 0.311 | 0.326
unlisted 200–220 kVA | KSA | 0.45856 | 0.46685 | 0.47929 | 0.50002 | 0.405 | 0.496
unlisted 200–220 kVA | UAE | 0.42266 | 0.4303 | 0.44176 | 0.46087 | 0.377 | 0.463
unlisted 300 kVA | KSA | 0.36442 | 0.30951 | 0.27454 | 0.2584 | 0.301 | 0.318
unlisted 300 kVA | UAE | 0.33589 | 0.28527 | 0.25304 | 0.23816 | 0.278 | 0.302
unlisted 500 kVA | KSA | 0.36495 | 0.31834 | 0.2896 | 0.2783 | 0.304 | 0.333
unlisted 500 kVA | UAE | 0.33637 | 0.29341 | 0.26692 | 0.25651 | 0.283 | 0.31
unlisted ≤125 kVA | KSA | 0.43908 | 0.41452 | 0.40231 | 0.40388 | 0.414 | 0.42
unlisted ≤125 kVA | UAE | 0.4047 | 0.38206 | 0.37081 | 0.37225 | 0.38 | 0.403
Low/high = 10th–90th percentile from 120 site-bootstrap refits. Loading = unit output ÷ rated kW (kVA × 0.8).

## Site check
Site | Months | Actual fuel (L) | Predicted, site left out (L) | Error | ¦Error¦
KSA - Sprint - I | 3 | 21907 | 18611 | -15.05% | 15.05%
UAE - Innovo Build - S | 10 | 145370 | 131054 | -9.848% | 9.848%
KSA - MBL Opera - S | 19 | 169614 | 154997 | -8.618% | 8.618%
UAE - Specialist - C | 7 | 238320 | 218074 | -8.495% | 8.495%
UAE - EAST VILLE Fujeirah - C | 14 | 1047206 | 983049 | -6.126% | 6.126%
UAE - Galfar - C | 11 | 1342047 | 1264903 | -5.748% | 5.748%
KSA - Namareq KAEC - C | 15 | 2406769 | 2270959 | -5.643% | 5.643%
UAE - ENATA - I | 1 | 21372 | 20336 | -4.847% | 4.847%
UAE - Intermass - S | 16 | 124843 | 120671 | -3.342% | 3.342%
KSA - Crystal Rabigh - C | 3 | 335751 | 324643 | -3.308% | 3.308%
KSA - ARCC (H) - C | 8 | 603167 | 586950 | -2.689% | 2.689%
UAE - Natural Fragrances - I | 1 | 8705 | 8557 | -1.7% | 1.7%
UAE - Nordic - I | 18 | 715245 | 706089 | -1.28% | 1.28%
KSA - Formula Arabia - C | 10 | 631455 | 628374 | -0.4879% | 0.4879%
KSA - MBL JCD Opera - S | 18 | 360684 | 358774 | -0.5295% | 0.5295%
KSA - AYTB Jubail - C | 18 | 2138484 | 2129509 | -0.4197% | 0.4197%
UAE - SJ ABED - C | 13 | 402977 | 403885 | 0.2253% | 0.2253%
KSA - Ramz Al Akhwa - C | 2 | 96470 | 96679 | 0.2166% | 0.2166%
UAE - Seven Brothers - C | 6 | 96781 | 97093 | 0.3224% | 0.3224%
KSA - Afnan - C | 13 | 540225 | 546342 | 1.132% | 1.132%
KSA - MBL Camp - C | 6 | 135544 | 137238 | 1.25% | 1.25%
KSA - ARAMCO PMT - C | 17 | 940646 | 952855 | 1.298% | 1.298%
KSA - Fame Fardani - C | 5 | 1093909 | 1109579 | 1.432% | 1.432%
KSA - AYTB Harad - C | 10 | 362846 | 367957 | 1.409% | 1.409%
KSA - MBL Oceanarium - S | 19 | 162508 | 165326 | 1.734% | 1.734%
UAE - Arabian Industries - C | 14 | 402260 | 409666 | 1.841% | 1.841%
UAE - Al Dar - S | 14 | 278316 | 287609 | 3.339% | 3.339%
UAE - MNH Fujairah - C | 4 | 211449 | 218692 | 3.425% | 3.425%
UAE - KITOPI Alqouz- I | 14 | 218897 | 226405 | 3.43% | 3.43%
UAE - Target - C | 11 | 2104264 | 2188507 | 4.003% | 4.003%
UAE - UG Camp - C | 17 | 1337096 | 1390534 | 3.997% | 3.997%
UAE - EAST VILLE Hubshan - C | 10 | 972173 | 1020558 | 4.977% | 4.977%
UAE - Trans Asia - I | 14 | 118080 | 124282 | 5.252% | 5.252%
KSA - Namariq Jizan - C | 6 | 1742118 | 1835838 | 5.38% | 5.38%
UAE - Techshore - I | 8 | 19271 | 21477 | 11.45% | 11.45%
UAE - AL Saida Fujeirah - C | 1 | 13951 | 15952 | 14.34% | 14.34%
KSA - KENT - C | 8 | 744631 | 881268 | 18.35% | 18.35%
Median ¦error¦ |  |  |  | 3.342%
Each site predicted with curves fitted on the other 36 sites, using the units that actually ran. KENT is the only Scania DC13 site, so left out it falls back to a generic 500 kVA curve.

## Fleet by family
Device | Family | Make | Engine | Year | Running hours | Country
GS-1250-003 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 | 2009 | 41619 | KSA
GS-1250-006 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 | 2009 | 13634 | UAE
GS-1250-010 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 | 2011 | 15261 | KSA
GS-1250-029 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 | 2013 | 20589 | UAE
GS-1250-030 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 | 2013 | 6687 | UAE
GS-1250-032 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 | 2013 | 9453 | KSA
GS-1250-036 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 | 2013 | 9987 | UAE
GS-1250-038 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 | 2013 | 9525 | UAE
GS-1250-041 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 | 2014 | 16520 | KSA
GS-1250-056 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 8912 | KSA
GS-1250-058 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 8948 | KSA
GS-1250-059 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 16950 | KSA
GS-1250-060 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 37209 | KSA
GS-1250-061 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 29707 | KSA
GS-1250-064 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 13564 | KSA
GS-1250-068 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 19262 | KSA
GS-1250-071 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 2788 | KSA
GS-1250-075 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 31595 | KSA
GS-1250-076 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 |  | 17644 | UAE
GS-1250-083 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 |  | 16516 | UAE
GS-1250-086 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50 G3 |  | 17722 | UAE
GS-1250-091 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 12814 | KSA
GS-1250-092 | Cummins KTA50 (1250 kVA) | CUMMINS | KTA50-G3 |  | 24655 | KSA
GS-350-019 | Cummins QSG12 (350 kVA) | CUMMINS | QSG12-G1 | 2024 | 9540 | UAE
GS-350-020 | Cummins QSG12 (350 kVA) | CUMMINS | QSG12-G1 | 2024 | 5692 | UAE
GS-350-021 | Cummins QSG12 (350 kVA) | CUMMINS | QSG12-G1 | 2024 | 7414 | UAE
GS-350-022 | Cummins QSG12 (350 kVA) | CUMMINS | QSG12-G1 | 2024 | 5948 | UAE
GS-800-024 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 8987 | UAE
GS-800-025 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 6116 | UAE
GS-800-026 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 8049 | UAE
GS-800-027 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 4375 | UAE
GS-800-028 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 8272 | UAE
GS-800-029 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 4305 | UAE
GS-800-030 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 9524 | UAE
GS-800-031 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 2607 | UAE
GS-800-032 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 9239 | UAE
GS-800-033 | Cummins QSK23 (800 kVA) | CUMMINS | QSK23-G3 | 2024 | 8122 | UAE
GS-250-001 | Cummins QSL9 (250–300 kVA) | CUMMINS | QSL9-G5 | 2024 | 8557 | UAE
GS-250-002 | Cummins QSL9 (250–300 kVA) | CUMMINS | QSL9-G5 | 2024 | 14669 | UAE
GS-250-003 | Cummins QSL9 (250–300 kVA) | CUMMINS | QSL9-G5 | 2024 | 7370 | UAE
GS-300-132 | Cummins QSL9 (250–300 kVA) | JCB | CUMMINS - QSL9 G5 | 2023 | 4128 | UAE
GS-300-133 | Cummins QSL9 (250–300 kVA) | JCB | CUMMINS - QSL9 G5 | 2023 | 14501 | UAE
GS-300-134 | Cummins QSL9 (250–300 kVA) | JCB | CUMMINS - QSL9 G5 | 2023 | 14724 | UAE
GS-1000-002 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2009 | 7570 | KSA
GS-1000-009 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2010 | 1729 | KSA
GS-1000-023 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2010 | 6068 | KSA
GS-1000-023 - N | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2010 | 6068 | KSA
GS-1000-023-N | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2010 | 6068 | KSA
GS-1000-038 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2010 | 9321 | UAE
GS-1000-046 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2010 |  | UAE
GS-1000-047 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2011 | 12274 | UAE → KSA
GS-1000-053 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2011 | 9485 | KSA
GS-1000-055 | Cummins QST30 (1000 kVA) | CUMMINS | QST30-G4 | 2011 | 5637 | KSA
GS-1000-074 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2017 | 16921 | UAE
GS-1000-075 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2017 |  | UAE
GS-1000-076 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2018 | 22432 | UAE
GS-1000-077 | Cummins QST30 (1000 kVA) | JCB | QST30-G4 | 2018 | 25849 | UAE
GS-500-017 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2009 | 45241 | KSA
GS-500-038 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2010 | 6301 | KSA
GS-500-040 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15 | 2010 | 16502 | UAE
GS-500-042 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15 | 2010 | 14247 | UAE
GS-500-048 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15 | 2013 | 51951 | UAE
GS-500-050 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2013 | 24979 | KSA
GS-500-065 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 27554 | KSA
GS-500-066 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 33138 | KSA
GS-500-067 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 36627 | KSA
GS-500-070 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 29351 | KSA
GS-500-072 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 36683 | KSA
GS-500-073 | Cummins QSX15 (500 kVA) | CUMMINS | QSX15-G8 | 2015 | 39028 | KSA
GS-125-070 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 21886 | UAE
GS-125-072 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 32715 | UAE
GS-125-080 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 24327 | UAE
GS-125-084 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 16424 | UAE
GS-125-086 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2017 | 18309 | KSA
GS-125-090 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2017 | 15727 | KSA
GS-125-091 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2017 | 21677 | KSA
GS-125-095 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2017 | 20802 | KSA
GS-125-099 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 21855 | UAE
GS-125-100 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 30549 | UAE
GS-125-104 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 26694 | UAE
GS-125-105 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 29055 | UAE
GS-125-105 BH need to confirm sim card | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 29055 | UAE
GS-125-107 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 15914 | UAE
GS-125-108 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 22910 | UAE
GS-125-111 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 17153 | UAE
GS-125-113 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 24665 | UAE
GS-125-113 BH need to confirm sim card | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2017 | 24665 | UAE
GS-125-117 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 31275 | UAE
GS-125-125 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 17529 | UAE
GS-125-126 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 18039 | UAE
GS-125-128 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 23510 | UAE
GS-125-141 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 21776 | UAE
GS-125-144 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 17230 | KSA
GS-125-148 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 22347 | KSA
GS-125-149 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 23901 | KSA
GS-125-151 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 19621 | KSA
GS-125-152 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 20481 | KSA
GS-125-153 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 23435 | KSA
GS-125-154 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 27669 | KSA
GS-125-154 - N | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 27669 | KSA
GS-125-156 | JCB 448 (125 kVA) | JCB | JCB 448 G-TCA 120 | 2018 | 20902 | KSA
GS-125-162 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 15300 | UAE
GS-125-163 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 21611 | UAE
GS-125-164 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 17983 | UAE
GS-125-169 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 9234 | UAE
GS-125-172 | JCB 448 (125 kVA) | JCB | JCB 448 TGAG-121 | 2018 | 15985 | UAE
GS-60-050 | JCB 448 (60 kVA) | JCB | JCB 448 TG-60 | 2018 | 35157 | UAE
GS-60-051 | JCB 448 (60 kVA) | JCB | JCB 448 TG-60 | 2018 | 24383 | UAE
GS-60-098 | JCB 448 (60 kVA) | JCB | JCB 448 TG-60 | 2018 | 21448 | UAE
GS-220-032 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2017 | 26072 | UAE
GS-220-033 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2017 | 34560 | UAE
GS-220-040 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2017 | 20724 | UAE → KSA
GS-220-043 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2017 | 22557 | KSA
GS-220-044 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2017 | 29934 | KSA
GS-220-050 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2017 | 27181 | KSA
GS-220-063 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 30531 | UAE
GS-220-067 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 17728 | UAE
GS-220-069 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 23491 | KSA
GS-220-070 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 30691 | UAE
GS-220-072 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 21215 | KSA
GS-220-083 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 27894 | UAE
GS-220-087 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 29038 | UAE
GS-220-088 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 33344 | KSA
GS-220-090 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 30207 | UAE
GS-220-091 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 25662 | KSA
GS-220-122 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 20553 | KSA
GS-220-126 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 12423 | UAE
GS-220-129 | JD 6068 (220 kVA) | JCB | JOHN DEERE - 6068HFU82 | 2018 | 19353 | KSA
GS-220-130 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 28931 | UAE
GS-220-136 | JD 6068 (220 kVA) | JCB | JOHN DEERE 6068HFU82 | 2018 | 20937 | UAE
GS-300-035 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 | 23678 | KSA
GS-300-038 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 | 26565 | KSA
GS-300-039 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 |  | KSA
GS-300-046 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 | 26830 | KSA
GS-300-050 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 | 28713 | KSA
GS-300-054 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 | 30376 | KSA
GS-300-056 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2017 |  | KSA
GS-300-065 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 26551 | UAE
GS-300-067 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 23502 | UAE
GS-300-068 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 21070 | KSA
GS-300-074 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 14435 | UAE
GS-300-076 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 26548 | UAE
GS-300-079 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 36055 | UAE
GS-300-080 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 10193 | UAE
GS-300-082 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 27810 | UAE
GS-300-084 new | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 |  | KSA
GS-300-086 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 24212 | UAE → KSA
GS-300-088 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2017 | 18888 | UAE
GS-300-091 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 20485 | KSA
GS-300-093 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 26495 | UAE
GS-300-095 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 22425 | UAE
GS-300-096 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 24197 | UAE
GS-300-098 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 16536 | UAE
GS-300-099 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 16559 | UAE
GS-300-101 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 29915 | KSA
GS-300-102 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 29717 | UAE
GS-300-113 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 18318 | UAE
GS-300-113 BH need to confirm sim card | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 18318 | UAE
GS-300-116 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 23754 | KSA
GS-300-117 | JD 6090 (300 kVA) | JCB | JOHN DEERE-6090HFU84 | 2018 | 25983 | UAE
GS-300-119 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 29672 | KSA
GS-300-121 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 24498 | KSA
GS-300-123 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 23790 | KSA
GS-300-127 | JD 6090 (300 kVA) | JCB | JOHN DEERE - 6090HFU84 | 2018 | 21499 | KSA
GS-500-113 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 13741 | KSA
GS-500-114 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 15369 | KSA
GS-500-115 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 14886 | KSA
GS-500-116 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 18035 | KSA
GS-500-117 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 12737 | KSA
GS-500-118 | Scania DC13 (500 kVA) | SCANIA | DC13 072A | 2024 | 14095 | KSA
GS-500-074 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 28796 | KSA
GS-500-074 - N | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 28796 | KSA
GS-500-075 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 29269 | KSA
GS-500-076 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 33393 | KSA
GS-500-077 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 31961 | KSA
GS-500-078 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 32544 | KSA
GS-500-079 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 33643 | KSA
GS-500-080 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 32315 | KSA
GS-500-081 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 32691 | KSA
GS-500-082 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 33634 | KSA
GS-500-083 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 30757 | KSA
GS-500-084 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 35477 | KSA
GS-500-084 - N | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 35477 | KSA
GS-500-085 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 29481 | KSA
GS-500-086 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 29680 | UAE
GS-500-087 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 14890 | UAE
GS-500-091 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 20760 | UAE
GS-500-092 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 16925 | UAE
GS-500-093 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 25627 | UAE
GS-500-094 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 38376 | UAE
GS-500-096 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 19394 | UAE
GS-500-097 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 21220 | UAE
GS-500-098 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 20615 | UAE
GS-500-104 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 26567 | KSA
GS-500-104 - N | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 26567 | KSA
GS-500-105 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 24787 | KSA
GS-500-106 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 6824 | KSA
GS-500-107 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 23212 | KSA
GS-500-108 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 22996 | KSA
GS-500-109 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 18740 | UAE
GS-500-110 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2018 | 17650 | UAE
GS-500-111 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2021 | 19620 | UAE
GS-500-112 | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2021 | 12346 | UAE
GS.500.077 New | Volvo TAD1651 (500 kVA) | JCB | VOLVO - TAD1651GE | 2017 | 31961 | KSA
CH-1125-1363 | unlisted |  |  |  |  | KSA
CH-300-388 | unlisted |  |  |  |  | KSA
CH-500-171 | unlisted |  |  |  |  | KSA
CH-500-185 | unlisted |  |  |  |  | KSA
CH-500-330 | unlisted |  |  |  |  | KSA
CH-500-341 | unlisted |  |  |  |  | KSA
CH-500-342 | unlisted |  |  |  |  | KSA
CH-500-426 | unlisted |  |  |  |  | KSA
CH-500-440 | unlisted |  |  |  |  | KSA
GS-300-388 | unlisted |  |  |  |  | KSA
GS-500-044 CH | unlisted |  |  |  |  | KSA
GS-500-045 CH | unlisted |  |  |  |  | KSA
GS-500-330 | unlisted |  |  |  |  | KSA
GS-500-336 | unlisted |  |  |  |  | KSA
GS-500-338 | unlisted |  |  |  |  | KSA
GS-500-341 | unlisted |  |  |  |  | KSA

## Model comparison
Model | Site-months | In-sample median | Leave-one-site-out: month median | month p90 | bias | site median | site p90 | site worst | 2026 test (fit on 2025): median | bias
kVA classes, no country | 384 | 4.481% | 5.947% | 15.86% | -0.04886% | 4.962% | 14.18% | 22.28% | 4.584% | 0.145%
kVA classes + country | 384 | 3.756% | 5.055% | 15.45% | -0.313% | 4.022% | 10.93% | 17.87% | 4.787% | 1.917%
engine families, no country | 384 | 3.662% | 6.356% | 14.52% | 0.4379% | 4.406% | 10.2% | 20.61% | 4.634% | 1.542%
engine families + country | 384 | 2.963% | 4.887% | 13.83% | 0.5218% | 3.342% | 10.49% | 18.35% | 3.64% | 2.106%