## Overview
Model vs actual, every site, every month with a month-end report
Site-months | 511
Sites | 37
Monthly L/kWh error, median of ¦error¦ | 5.951%
Monthly L/kWh error, 90th percentile of ¦error¦ | 18.7%
Share of months within ±10% | 72.21%
Bias (median error, + = model high) | 0.78%
Fleet fuel, actual (L) | 30925998
Fleet fuel, model (L) | 31219235
Fleet fuel error | 0.9482%
How to read
Each site-month was simulated from the site's hourly generator demand (unit counters, scaled to the month-end DG kWh so the kWh basis is the site meter).
The PMS start/stop settings come from the site's own 1-minute data for that quarter (pms_source = quarter), else the site median, else a default by site type.
Fuel per unit comes from the engine-family curves fitted with THAT SITE LEFT OUT, so every number is an out-of-sample prediction.
"Curves on actual running" applies the same curves to what the units really did; the gap between it and the model is the dispatch model's own error.
Actual = month-end Hybrid Performance Report fuel and DG kWh. Months with fewer than 20 days of hourly data, or where the report DG differs from the portal meter by more than 20% (site changes, partial billing months), are listed on the Excluded months tab and left out of the statistics.

## Site-months
Site | Month | Country | Type | Days of hourly data | Fleet (kVA) | Engine families | Actual fuel (L) | Actual DG kWh | Actual L/kWh | Solar share of load | Model fuel (L) | Model L/kWh | Curves on actual running (L) | PMS start | PMS stop | Model error | ¦Model error¦ | PMS setting source | Sim mean loading | Site-meter ratio (report DG / unit counters)
KSA - ARAMCO PMT - C | 2025-01 | KSA | C | 24 | 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 39000 | 105059 | 0.37122 | 6.6% | 36497 | 0.3474 | 36619 | 0.49 | 0.3 | -6.418% | 6.418% | quarter | 0.34 | 1.017
KSA - ARAMCO PMT - C | 2025-02 | KSA | C | 28 | 500 + 300 + 500 + 500 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 38165 | 87845 | 0.43446 | 7.1% | 30939 | 0.3522 | 34784 | 0.49 | 0.3 | -18.93% | 18.93% | quarter | 0.32 | 1
KSA - ARAMCO PMT - C | 2025-03 | KSA | C | 31 | 300 + 500 + 500 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 46706 | 100676 | 0.46392 | 10% | 43702 | 0.43409 | 41402 | 0.49 | 0.3 | -6.432% | 6.432% | quarter | 0.27 | 0.994
KSA - ARAMCO PMT - C | 2025-04 | KSA | C | 30 | 500 + 300 + 500 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 59320 | 165755 | 0.35788 | 6.2% | 58325 | 0.35187 | 57590 | 0.58 | 0.41 | -1.677% | 1.677% | quarter | 0.43 | 1.084
KSA - ARAMCO PMT - C | 2025-06 | KSA | C | 30 | 500 + 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 78300 | 218465 | 0.35841 | 5.3% | 72567 | 0.33217 | 74100 | 0.58 | 0.41 | -7.322% | 7.322% | quarter | 0.45 | 1.056
KSA - ARAMCO PMT - C | 2025-07 | KSA | C | 28 | 500 + 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 83564 | 265004 | 0.31533 | 4.3% | 86474 | 0.32631 | 88992 | 0.7 | 0.43 | 3.482% | 3.482% | quarter | 0.52 | 1.244
KSA - ARAMCO PMT - C | 2025-08 | KSA | C | 31 | 500 + 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 86929 | 278672 | 0.31194 | 3.8% | 90663 | 0.32534 | 94614 | 0.7 | 0.43 | 4.295% | 4.295% | quarter | 0.55 | 1.04
KSA - ARAMCO PMT - C | 2025-09 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 68202 | 218730 | 0.31181 | 4.5% | 71410 | 0.32648 | 71882 | 0.7 | 0.43 | 4.704% | 4.704% | quarter | 0.51 | 1.022
KSA - ARAMCO PMT - C | 2025-10 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 49800 | 149198 | 0.33378 | 5.8% | 49914 | 0.33455 | 50743 | 0.72 | 0.41 | 0.2289% | 0.2289% | quarter | 0.43 | 0.998
KSA - ARAMCO PMT - C | 2025-11 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 36440 | 104601 | 0.34837 | 6.9% | 35797 | 0.34222 | 35875 | 0.72 | 0.41 | -1.765% | 1.765% | quarter | 0.36 | 0.96
KSA - ARAMCO PMT - C | 2025-12 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 35526 | 109516 | 0.32439 | 5.4% | 37381 | 0.34133 | 37574 | 0.72 | 0.41 | 5.222% | 5.222% | quarter | 0.37 | 1
KSA - ARAMCO PMT - C | 2026-01 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 33047 | 98284 | 0.33624 | 7.4% | 35958 | 0.36586 | 34251 | 0.45 | 0.16 | 8.809% | 8.809% | quarter | 0.29 | 1.014
KSA - ARAMCO PMT - C | 2026-02 | KSA | C | 28 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 28532 | 83476 | 0.3418 | 9.1% | 29881 | 0.35796 | 29546 | 0.45 | 0.16 | 4.728% | 4.728% | quarter | 0.3 | 0.996
KSA - ARAMCO PMT - C | 2026-03 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 31823 | 93504 | 0.34034 | 8.6% | 33717 | 0.36059 | 33164 | 0.45 | 0.16 | 5.952% | 5.952% | quarter | 0.3 | 0.999
KSA - ARAMCO PMT - C | 2026-04 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 36079 | 111671 | 0.32308 | 7.5% | 37886 | 0.33926 | 37995 | 0.71 | 0.36 | 5.008% | 5.008% | quarter | 0.39 | 1.017
KSA - ARAMCO PMT - C | 2026-05 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 56362 | 176643 | 0.31907 | 6% | 57977 | 0.32822 | 57435 | 0.71 | 0.36 | 2.865% | 2.865% | quarter | 0.49 | 1.25
KSA - ARAMCO PMT - C | 2026-06 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 70546 | 222592 | 0.31693 | 4.9% | 72589 | 0.32611 | 73960 | 0.71 | 0.36 | 2.896% | 2.896% | quarter | 0.51 | 1.029
KSA - ARAMCO PMT - C | 2026-07 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 81394 | 239877 | 0.33932 | 5.1% | 78064 | 0.32543 | 79944 | 0.71 | 0.36 | -4.091% | 4.091% | quarter | 0.53 | 1.003
KSA - ARAMCO PMT - C | 2026-08 | KSA | C | 31 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 88608 | 276719 | 0.32021 | 4% | 90191 | 0.32593 | 90713 | 0.71 | 0.36 | 1.787% | 1.787% | quarter | 0.54 | 1.09
KSA - ARAMCO PMT - C | 2026-09 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 71229 | 220073 | 0.32366 | 4.2% | 71810 | 0.3263 | 72114 | 0.71 | 0.36 | 0.8157% | 0.8157% | quarter | 0.51 | 1.062
KSA - ARCC (H) - C | 2025-01 | KSA | C | 27 | 1250 + 1250 + 300 + 300 | Cummins KTA50 (1250 kVA), JD 6090 (300 kVA) | 62000 | 108262 | 0.57268 | 0% | 56371 | 0.52069 | 53524 | 0.67 | 0.33 | -9.079% | 9.079% | quarter | 0.16 | 1.25
KSA - ARCC (H) - C | 2025-02 | KSA | C | 25 | 1250 + 300 + 300 + 500 + 1250 + 500 | Cummins KTA50 (1250 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 49450 | 96677 | 0.5115 | 0% | 49307 | 0.51002 | 42668 | 0.67 | 0.33 | -0.2892% | 0.2892% | quarter | 0.17 | 1.216
KSA - ARCC (H) - C | 2025-03 | KSA | C | 31 | 500 + 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 41238 | 128473 | 0.32099 | 0% | 42928 | 0.33414 | 43113 | 0.67 | 0.33 | 4.098% | 4.098% | quarter | 0.39 | 1.121
KSA - ARCC (H) - C | 2025-05 | KSA | C | 31 | 1250 + 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 114800 | 313553 | 0.36613 | 0% | 107183 | 0.34183 | 103548 | 0.56 | 0.35 | -6.635% | 6.635% | quarter | 0.37 | 1.008
KSA - ARCC (H) - C | 2025-06 | KSA | C | 30 | 1250 + 500 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 128307 | 369690 | 0.34707 | 0% | 120526 | 0.32602 | 119668 | 0.56 | 0.35 | -6.064% | 6.064% | quarter | 0.44 | 1.036
KSA - ARCC (H) - C | 2025-07 | KSA | C | 31 | 1250 + 500 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 133216 | 405979 | 0.32814 | 0% | 130857 | 0.32232 | 129923 | 0.56 | 0.4 | -1.771% | 1.771% | quarter | 0.46 | 1.011
KSA - ARCC (H) - C | 2025-08 | KSA | C | 31 | 1250 + 500 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 129237 | 407477 | 0.31716 | 0% | 131668 | 0.32313 | 129875 | 0.56 | 0.4 | 1.881% | 1.881% | quarter | 0.45 | 1.062
KSA - ARCC (H) - C | 2025-09 | KSA | C | 30 | 1250 + 500 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 93058 | 279949 | 0.33241 | 0% | 96899 | 0.34613 | 92937 | 0.56 | 0.4 | 4.128% | 4.128% | quarter | 0.36 | 1.045
KSA - ARCC (H) - C | 2025-10 | KSA | C | 31 | 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 61205 | 188832 | 0.32412 | 0% | 73523 | 0.38936 | 62270 | 0.45 | 0.22 | 20.13% | 20.13% | quarter | 0.28 | 1.25
KSA - ARCC (H) - C | 2025-11 | KSA | C | 30 | 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 42811 | 117478 | 0.36442 | 0% | 48836 | 0.4157 | 43035 | 0.45 | 0.22 | 14.07% | 14.07% | quarter | 0.26 | 1.014
KSA - ARCC (H) - C | 2025-12 | KSA | C | 31 | 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 32901 | 84142 | 0.39102 | 0% | 32829 | 0.39016 | 32843 | 0.45 | 0.22 | -0.2188% | 0.2188% | quarter | 0.26 | 1.031
KSA - ARCC (H) - C | 2026-01 | KSA | C | 31 | 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 27723 | 67564 | 0.41032 | 0% | 26306 | 0.38935 | 26316 | 0.45 | 0.3 | -5.111% | 5.111% | quarter | 0.23 | 1.015
KSA - ARCC (H) - C | 2026-02 | KSA | C | 28 | 500 + 1250 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA) | 30351 | 61809 | 0.49104 | 0% | 24245 | 0.39226 | 32093 | 0.45 | 0.3 | -20.12% | 20.12% | quarter | 0.23 | 1.087
KSA - AYTB Harad - C | 2025-02 | KSA | C | 26 | 300 + 300 + 500 + 500 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 43500 | 64195 | 0.67762 | 6.1% | 31013 | 0.48311 | 26351 | 0.45 | 0.2 | -28.71% | 28.71% | quarter | 0.29 | 1.25
KSA - AYTB Harad - C | 2025-03 | KSA | C | 31 | 500 + 300 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 21240 | 64442 | 0.3296 | 22% | 25683 | 0.39854 | 26503 | 0.45 | 0.2 | 20.92% | 20.92% | quarter | 0.21 | 0.966
KSA - AYTB Harad - C | 2025-06 | KSA | C | 30 | 500 + 300 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 57528 | 160969 | 0.35739 | 22.9% | 63708 | 0.39578 | 54738 | 0.45 | 0.18 | 10.74% | 10.74% | quarter | 0.28 | 1.068
KSA - AYTB Harad - C | 2025-07 | KSA | C | 31 | 500 + 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 55134 | 156120 | 0.35315 | 21.9% | 46968 | 0.30085 | 49055 | 0.73 | 0.34 | -14.81% | 14.81% | quarter | 0.47 | 1.094
KSA - AYTB Harad - C | 2025-08 | KSA | C | 31 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA), unlisted 500 kVA | 45530 | 154950 | 0.29384 | 20.4% | 46710 | 0.30145 | 46593 | 0.73 | 0.34 | 2.592% | 2.592% | quarter | 0.46 | 1.009
KSA - AYTB Harad - C | 2025-09 | KSA | C | 30 | 500 + 500 + 500 + 500 | Volvo TAD1651 (500 kVA), unlisted 500 kVA | 35467 | 115359 | 0.30745 | 22.9% | 36555 | 0.31688 | 36377 | 0.73 | 0.34 | 3.068% | 3.068% | quarter | 0.39 | 1.052
KSA - AYTB Harad - C | 2025-10 | KSA | C | 31 | 500 + 300 + 500 + 500 | Volvo TAD1651 (500 kVA), unlisted 300 kVA, unlisted 500 kVA | 26738 | 78396 | 0.34106 | 27.4% | 30152 | 0.38461 | 28705 | 0.45 | 0.25 | 12.77% | 12.77% | quarter | 0.25 | 1.009
KSA - AYTB Harad - C | 2025-11 | KSA | C | 30 | 300 + 500 + 500 | Volvo TAD1651 (500 kVA), unlisted 300 kVA | 20998 | 67858 | 0.30944 | 22.5% | 23620 | 0.34808 | 20497 | 0.45 | 0.25 | 12.49% | 12.49% | quarter | 0.28 | 1.033
KSA - AYTB Harad - C | 2025-12 | KSA | C | 27 | 300 + 300 + 500 + 500 | Volvo TAD1651 (500 kVA), unlisted 300 kVA | 17099 | 52560 | 0.32532 | 15.9% | 16854 | 0.32066 | 16217 | 0.45 | 0.25 | -1.433% | 1.433% | quarter | 0.3 | 1.002
KSA - AYTB Jubail - C | 2025-02 | KSA | C | 28 | 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 63651 | 183526 | 0.34682 | 0% | 57953 | 0.31578 | 59087 | 0.45 | 0.21 | -8.952% | 8.952% | quarter | 0.34 | 1.051
KSA - AYTB Jubail - C | 2025-03 | KSA | C | 30 | 1250 + 1000 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 78309 | 231598 | 0.33812 | 0% | 80560 | 0.34784 | 75843 | 0.45 | 0.21 | 2.875% | 2.875% | quarter | 0.31 | 1.019
KSA - AYTB Jubail - C | 2025-05 | KSA | C | 31 | 1000 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 144953 | 427984 | 0.33869 | 0% | 134336 | 0.31388 | 134241 | 0.61 | 0.34 | -7.324% | 7.324% | quarter | 0.42 | 0.905
KSA - AYTB Jubail - C | 2025-06 | KSA | C | 30 | 1250 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 209986 | 636538 | 0.32989 | 0% | 200454 | 0.31491 | 198352 | 0.61 | 0.34 | -4.539% | 4.539% | quarter | 0.46 | 1.109
KSA - AYTB Jubail - C | 2025-07 | KSA | C | 31 | 1250 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 216783 | 669193 | 0.32395 | 2.9% | 210379 | 0.31438 | 209063 | 0.6 | 0.4 | -2.954% | 2.954% | quarter | 0.46 | 0.969
KSA - AYTB Jubail - C | 2025-08 | KSA | C | 31 | 1250 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 204413 | 684968 | 0.29843 | 8.5% | 214925 | 0.31377 | 213591 | 0.6 | 0.4 | 5.143% | 5.143% | quarter | 0.47 | 1.027
KSA - AYTB Jubail - C | 2025-09 | KSA | C | 30 | 1250 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 156832 | 530936 | 0.29539 | 8.7% | 167417 | 0.31532 | 165196 | 0.6 | 0.4 | 6.749% | 6.749% | quarter | 0.46 | 0.993
KSA - AYTB Jubail - C | 2025-10 | KSA | C | 31 | 1000 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 97582 | 327926 | 0.29757 | 13.3% | 105860 | 0.32282 | 101677 | 0.49 | 0.29 | 8.483% | 8.483% | quarter | 0.34 | 0.965
KSA - AYTB Jubail - C | 2025-11 | KSA | C | 30 | 1000 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA) | 60693 | 189622 | 0.32007 | 16.5% | 59523 | 0.3139 | 60137 | 0.49 | 0.29 | -1.928% | 1.928% | quarter | 0.3 | 0.976
KSA - AYTB Jubail - C | 2025-12 | KSA | C | 31 | 500 + 1250 + 1000 + 500 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA), unlisted 500 kVA | 50539 | 156323 | 0.3233 | 15.1% | 62709 | 0.40115 | 50699 | 0.49 | 0.29 | 24.08% | 24.08% | quarter | 0.24 | 0.982
KSA - AYTB Jubail - C | 2026-01 | KSA | C | 31 | 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 50147 | 150894 | 0.33233 | 17.3% | 62963 | 0.41727 | 51841 | 0.45 | 0.21 | 25.56% | 25.56% | quarter | 0.2 | 0.882
KSA - AYTB Jubail - C | 2026-02 | KSA | C | 28 | 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 63293 | 172902 | 0.36606 | 17.1% | 67353 | 0.38954 | 57997 | 0.45 | 0.21 | 6.415% | 6.415% | quarter | 0.23 | 0.93
KSA - AYTB Jubail - C | 2026-03 | KSA | C | 31 | 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 63147 | 205606 | 0.30713 | 18.6% | 77753 | 0.37817 | 66372 | 0.45 | 0.21 | 23.13% | 23.13% | quarter | 0.25 | 1.039
KSA - AYTB Jubail - C | 2026-04 | KSA | C | 30 | 1250 + 500 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 74727 | 236711 | 0.31569 | 23.7% | 83394 | 0.3523 | 77659 | 0.62 | 0.43 | 11.6% | 11.6% | quarter | 0.32 | 0.955
KSA - AYTB Jubail - C | 2026-05 | KSA | C | 31 | 500 + 1250 + 1250 + 500 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 128694 | 410913 | 0.31319 | 24.5% | 133325 | 0.32446 | 131155 | 0.62 | 0.43 | 3.598% | 3.598% | quarter | 0.4 | 0.985
KSA - AYTB Jubail - C | 2026-06 | KSA | C | 30 | 500 + 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 137865 | 461599 | 0.29867 | 28.4% | 144484 | 0.31301 | 142638 | 0.62 | 0.43 | 4.801% | 4.801% | quarter | 0.44 | 0.952
KSA - AYTB Jubail - C | 2026-07 | KSA | C | 31 | 1250 + 500 + 500 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 174308 | 552476 | 0.3155 | 27% | 175295 | 0.31729 | 174914 | 0.53 | 0.41 | 0.5662% | 0.5662% | quarter | 0.43 | 0.931
KSA - AYTB Jubail - C | 2026-08 | KSA | C | 31 | 1250 + 500 + 500 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 202825 | 647686 | 0.31315 | 23.5% | 203782 | 0.31463 | 205117 | 0.53 | 0.41 | 0.4718% | 0.4718% | quarter | 0.45 | 0.967
KSA - AYTB Jubail - C | 2026-09 | KSA | C | 30 | 500 + 1250 + 500 + 1250 + 500 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 176520 | 557700 | 0.31651 | 23.7% | 177924 | 0.31903 | 175385 | 0.53 | 0.41 | 0.7954% | 0.7954% | quarter | 0.41 | 0.962
KSA - Afnan - C | 2025-05 | KSA | C | 31 | 500 + 500 + 300 | Volvo TAD1651 (500 kVA), unlisted 300 kVA | 59617 | 165248 | 0.36077 | 6.7% | 54240 | 0.32823 | 54314 | 0.69 | 0.34 | -9.019% | 9.019% | quarter | 0.44 | 1.051
KSA - Afnan - C | 2025-06 | KSA | C | 30 | 500 + 500 + 300 | Volvo TAD1651 (500 kVA), unlisted 300 kVA | 64100 | 184671 | 0.3471 | 5.8% | 60148 | 0.3257 | 60282 | 0.69 | 0.34 | -6.165% | 6.165% | quarter | 0.48 | 1.045
KSA - Afnan - C | 2025-07 | KSA | C | 31 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 74143 | 220137 | 0.3368 | 4.8% | 71331 | 0.32403 | 72117 | 0.71 | 0.36 | -3.793% | 3.793% | quarter | 0.51 | 1.006
KSA - Afnan - C | 2025-08 | KSA | C | 31 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 72689 | 230448 | 0.31542 | 4.2% | 74589 | 0.32367 | 75121 | 0.71 | 0.36 | 2.614% | 2.614% | quarter | 0.52 | 1.001
KSA - Afnan - C | 2025-09 | KSA | C | 30 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 54976 | 172224 | 0.31921 | 5% | 56128 | 0.3259 | 56430 | 0.71 | 0.36 | 2.095% | 2.095% | quarter | 0.48 | 1.015
KSA - Afnan - C | 2025-10 | KSA | C | 31 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 34075 | 98040 | 0.34756 | 8.4% | 33836 | 0.34512 | 33950 | 0.69 | 0.35 | -0.7014% | 0.7014% | quarter | 0.33 | 1.005
KSA - Afnan - C | 2025-11 | KSA | C | 30 | 500 + 500 + 500 | Volvo TAD1651 (500 kVA) | 26291 | 64727 | 0.40618 | 9.7% | 24689 | 0.38143 | 24731 | 0.69 | 0.35 | -6.093% | 6.093% | quarter | 0.23 | 1.061
KSA - Afnan - C | 2025-12 | KSA | C | 31 | 500 + 500 + 300 + 220 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 24786 | 59757 | 0.41478 | 6.8% | 23735 | 0.39719 | 23633 | 0.69 | 0.35 | -4.24% | 4.24% | quarter | 0.2 | 1.002
KSA - Afnan - C | 2026-01 | KSA | C | 31 | 300 + 220 + 500 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 22358 | 71539 | 0.31253 | 6.3% | 25662 | 0.35871 | 25821 | 0.77 | 0.43 | 14.78% | 14.78% | quarter | 0.37 | 1.009
KSA - Afnan - C | 2026-02 | KSA | C | 28 | 300 + 220 + 500 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 18955 | 59425 | 0.31897 | 8.8% | 21190 | 0.35658 | 21245 | 0.77 | 0.43 | 11.79% | 11.79% | quarter | 0.36 | 1.01
KSA - Afnan - C | 2026-03 | KSA | C | 31 | 300 + 220 + 500 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 22370 | 75343 | 0.29691 | 7.9% | 26454 | 0.35111 | 26482 | 0.77 | 0.43 | 18.26% | 18.26% | quarter | 0.4 | 1.015
KSA - Afnan - C | 2026-04 | KSA | C | 30 | 300 + 500 + 220 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 25083 | 79492 | 0.31554 | 10.7% | 27499 | 0.34593 | 27692 | 0.71 | 0.35 | 9.632% | 9.632% | quarter | 0.4 | 0.99
KSA - Afnan - C | 2026-05 | KSA | C | 31 | 300 + 500 + 500 + 220 | JD 6068 (220 kVA), Volvo TAD1651 (500 kVA), unlisted 300 kVA | 40782 | 128010 | 0.31858 | 7.9% | 42750 | 0.33396 | 42689 | 0.71 | 0.35 | 4.826% | 4.826% | quarter | 0.47 | 1.08
KSA - Afnan - C | 2026-06 | KSA | C | 30 | 500 + 300 + 500 | Volvo TAD1651 (500 kVA), unlisted 300 kVA | 29067 | 83678 | 0.34737 | 11.9% | 29185 | 0.34878 | 28669 | 0.71 | 0.35 | 0.406% | 0.406% | quarter | 0.31 | 1.25
KSA - Crystal Rabigh - C | 2025-02 | KSA | C | 26 | 500 + 500 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 40133 | 112354 | 0.3572 | 10.7% | 37440 | 0.33323 | 38205 | 0.63 | 0.33 | -6.71% | 6.71% | quarter | 0.41 | 1.087
KSA - Crystal Rabigh - C | 2025-03 | KSA | C | 31 | 500 + 500 + 500 + 300 + 1000 | Cummins QST30 (1000 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 92539 | 275210 | 0.33625 | 7% | 90835 | 0.33006 | 89940 | 0.63 | 0.33 | -1.841% | 1.841% | quarter | 0.44 | 1.016
KSA - Crystal Rabigh - C | 2025-05 | KSA | C | 29 | 500 + 1250 + 1000 + 500 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 162052 | 444898 | 0.36425 | 5% | 144104 | 0.3239 | 138198 | 0.66 | 0.42 | -11.08% | 11.08% | quarter | 0.44 | 1.171
KSA - Crystal Rabigh - C | 2025-06 | KSA | C | 29 | 1000 + 500 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 131057 | 418506 | 0.31315 | 5.4% | 128712 | 0.30755 | 128573 | 0.66 | 0.42 | -1.789% | 1.789% | quarter | 0.49 | 0.988
KSA - Crystal Rabigh - C | 2025-07 | KSA | C | 31 | 1000 + 500 + 1250 | Cummins KTA50 (1250 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 112155 | 352342 | 0.31831 | 6.1% | 106581 | 0.30249 | 106627 | 0.66 | 0.43 | -4.97% | 4.97% | quarter | 0.49 | 0.967
KSA - Fame Fardani - C | 2026-05 | KSA | C | 31 | 500 + 1250 + 500 + 1250 + 500 | Cummins KTA50 (1250 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 157342 | 516223 | 0.30479 | 0% | 162171 | 0.31415 | 156450 | 0.74 | 0.49 | 3.069% | 3.069% | quarter | 0.47 | 0.988
KSA - Fame Fardani - C | 2026-06 | KSA | C | 30 | 500 + 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 198452 | 654121 | 0.30339 | 4.7% | 198486 | 0.30344 | 199165 | 0.74 | 0.49 | 0.01713% | 0.01713% | quarter | 0.55 | 1.022
KSA - Fame Fardani - C | 2026-07 | KSA | C | 31 | 500 + 500 + 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 228232 | 756449 | 0.30171 | 7.2% | 232876 | 0.30785 | 232639 | 0.66 | 0.49 | 2.035% | 2.035% | quarter | 0.5 | 0.949
KSA - Fame Fardani - C | 2026-08 | KSA | C | 31 | 1250 + 500 + 500 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 284741 | 958885 | 0.29695 | 5.1% | 293784 | 0.30638 | 293073 | 0.66 | 0.49 | 3.176% | 3.176% | quarter | 0.55 | 1.026
KSA - Fame Fardani - C | 2026-09 | KSA | C | 30 | 500 + 1250 + 500 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 500 kVA | 225142 | 742778 | 0.30311 | 11.4% | 229614 | 0.30913 | 229075 | 0.66 | 0.49 | 1.986% | 1.986% | quarter | 0.51 | 0.968
KSA - Formula Arabia - C | 2025-12 | KSA | C | 31 | 500 + 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 48838 | 128206 | 0.38093 | 0% | 44490 | 0.34702 | 44978 | 0.47 | 0.28 | -8.903% | 8.903% | quarter | 0.33 | 1.022
KSA - Formula Arabia - C | 2026-01 | KSA | C | 31 | 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 44041 | 126893 | 0.34707 | 0% | 42343 | 0.33369 | 42607 | 0.67 | 0.33 | -3.855% | 3.855% | quarter | 0.4 | 1
KSA - Formula Arabia - C | 2026-02 | KSA | C | 28 | 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 43850 | 133181 | 0.32925 | 5.6% | 43984 | 0.33026 | 44114 | 0.67 | 0.33 | 0.3056% | 0.3056% | quarter | 0.43 | 1.01
KSA - Formula Arabia - C | 2026-03 | KSA | C | 31 | 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 34501 | 99937 | 0.34523 | 34.5% | 35137 | 0.35159 | 35345 | 0.67 | 0.33 | 1.843% | 1.843% | quarter | 0.32 | 1.005
KSA - Formula Arabia - C | 2026-04 | KSA | C | 30 | 500 + 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 50529 | 147072 | 0.34357 | 31.3% | 49255 | 0.3349 | 49976 | 0.66 | 0.32 | -2.521% | 2.521% | quarter | 0.4 | 0.99
KSA - Formula Arabia - C | 2026-05 | KSA | C | 31 | 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 65620 | 195950 | 0.33488 | 29.2% | 64690 | 0.33014 | 65246 | 0.66 | 0.32 | -1.417% | 1.417% | quarter | 0.43 | 1.006
KSA - Formula Arabia - C | 2026-06 | KSA | C | 30 | 500 + 500 + 500 | Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 72070 | 218178 | 0.33033 | 27.4% | 71364 | 0.32709 | 71730 | 0.66 | 0.32 | -0.9796% | 0.9796% | quarter | 0.45 | 0.995
KSA - Formula Arabia - C | 2026-07 | KSA | C | 31 | 500 + 500 + 500 + 300 + 300 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 87200 | 268722 | 0.3245 | 22.7% | 87628 | 0.32609 | 89094 | 0.62 | 0.35 | 0.4908% | 0.4908% | quarter | 0.46 | 0.988
KSA - Formula Arabia - C | 2026-08 | KSA | C | 31 | 500 + 500 + 300 + 300 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 95844 | 292160 | 0.32805 | 21.2% | 99215 | 0.33959 | 96593 | 0.62 | 0.35 | 3.517% | 3.517% | quarter | 0.47 | 1.035
KSA - Formula Arabia - C | 2026-09 | KSA | C | 30 | 500 + 500 + 300 + 300 + 300 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 88962 | 257169 | 0.34593 | 20.9% | 86197 | 0.33518 | 89255 | 0.62 | 0.35 | -3.108% | 3.108% | quarter | 0.45 | 1.02
KSA - KENT - C | 2026-02 | KSA | C | 28 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 46699 | 161445 | 0.28926 | 15.5% | 54134 | 0.33531 | 55569 | 0.56 | 0.29 | 15.92% | 15.92% | quarter | 0.4 | 0.992
KSA - KENT - C | 2026-03 | KSA | C | 31 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 56622 | 200928 | 0.2818 | 13.1% | 67554 | 0.33621 | 68174 | 0.56 | 0.29 | 19.31% | 19.31% | quarter | 0.39 | 1
KSA - KENT - C | 2026-04 | KSA | C | 30 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 64690 | 235197 | 0.27505 | 11.9% | 78206 | 0.33251 | 78662 | 0.58 | 0.35 | 20.89% | 20.89% | quarter | 0.41 | 1.002
KSA - KENT - C | 2026-05 | KSA | C | 31 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 92809 | 336083 | 0.27615 | 10.7% | 110058 | 0.32747 | 108836 | 0.58 | 0.35 | 18.59% | 18.59% | quarter | 0.44 | 1.065
KSA - KENT - C | 2026-06 | KSA | C | 30 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 108059 | 389187 | 0.27765 | 9.7% | 127207 | 0.32685 | 127787 | 0.58 | 0.35 | 17.72% | 17.72% | quarter | 0.45 | 0.996
KSA - KENT - C | 2026-07 | KSA | C | 31 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 121410 | 429394 | 0.28275 | 9.1% | 138595 | 0.32277 | 140797 | 0.62 | 0.38 | 14.15% | 14.15% | quarter | 0.49 | 0.968
KSA - KENT - C | 2026-08 | KSA | C | 31 | 500 + 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 139844 | 506413 | 0.27615 | 7.1% | 164243 | 0.32433 | 164337 | 0.62 | 0.38 | 17.45% | 17.45% | quarter | 0.47 | 1.041
KSA - KENT - C | 2026-09 | KSA | C | 30 | 500 + 500 + 500 + 500 + 500 | Scania DC13 (500 kVA) | 114498 | 421033 | 0.27195 | 7.6% | 136093 | 0.32324 | 135927 | 0.62 | 0.38 | 18.86% | 18.86% | quarter | 0.49 | 1.008
KSA - MBL Camp - C | 2026-02 | KSA | C | 26 | 220 + 500 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), Volvo TAD1651 (500 kVA) | 4200 | 12520 | 0.33546 | 0% | 6122 | 0.48898 | 6151 | 0.45 | 0.09 | 45.76% | 45.76% | quarter | 0.25 | 1.073
KSA - MBL Camp - C | 2026-03 | KSA | C | 25 | 220 + 500 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), Volvo TAD1651 (500 kVA) | 8206 | 13174 | 0.62289 | 0% | 7917 | 0.60096 | 8046 | 0.45 | 0.09 | -3.522% | 3.522% | quarter | 0.16 | 0.964
KSA - MBL Camp - C | 2026-05 | KSA | C | 30 | 220 + 500 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), Volvo TAD1651 (500 kVA) | 16061 | 26993 | 0.59501 | 20.8% | 13395 | 0.49624 | 13434 | 0.45 | 0.2 | -16.6% | 16.6% | quarter | 0.24 | 0.983
KSA - MBL Camp - C | 2026-06 | KSA | C | 30 | 220 + 500 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), Volvo TAD1651 (500 kVA) | 21144 | 51438 | 0.41106 | 24.6% | 24389 | 0.47414 | 21193 | 0.45 | 0.2 | 15.35% | 15.35% | quarter | 0.22 | 0.982
KSA - MBL Camp - C | 2026-07 | KSA | C | 31 | 300 + 220 + 500 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 26830 | 63550 | 0.42219 | 23.9% | 30928 | 0.48667 | 29158 | 0.49 | 0.26 | 15.27% | 15.27% | quarter | 0.31 | 0.961
KSA - MBL Camp - C | 2026-08 | KSA | C | 31 | 220 + 300 + 500 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 33300 | 77595 | 0.42915 | 20.1% | 36264 | 0.46735 | 35610 | 0.49 | 0.26 | 8.901% | 8.901% | quarter | 0.32 | 1.074
KSA - MBL Camp - C | 2026-09 | KSA | C | 30 | 220 + 300 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 30003 | 63289 | 0.47406 | 19.3% | 30004 | 0.47408 | 29244 | 0.49 | 0.26 | 0.003333% | 0.003333% | quarter | 0.31 | 1.057
KSA - MBL JCD Opera - S | 2025-01 | KSA | S | 27 | 125 + 125 + 220 + 300 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 14582 | 36564 | 0.39881 | 12.7% | 15115 | 0.41338 | 15128 | 0.49 | 0.25 | 3.655% | 3.655% | quarter | 0.34 | 1.25
KSA - MBL JCD Opera - S | 2025-02 | KSA | S | 25 | 125 + 125 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 11650 | 27904 | 0.4175 | 25.5% | 11664 | 0.418 | 11830 | 0.49 | 0.25 | 0.1202% | 0.1202% | quarter | 0.33 | 1.191
KSA - MBL JCD Opera - S | 2025-03 | KSA | S | 31 | 125 + 125 + 220 + 125 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 14247 | 29877 | 0.47686 | 28.6% | 12448 | 0.41664 | 14911 | 0.49 | 0.25 | -12.63% | 12.63% | quarter | 0.34 | 0.962
KSA - MBL JCD Opera - S | 2025-04 | KSA | S | 30 | 125 + 125 + 300 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 17250 | 39879 | 0.43256 | 32.4% | 16700 | 0.41877 | 17752 | 0.45 | 0.19 | -3.188% | 3.188% | site | 0.33 | 1.142
KSA - MBL JCD Opera - S | 2025-06 | KSA | S | 30 | 125 + 125 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 17300 | 38783 | 0.44607 | 36.6% | 16347 | 0.4215 | 16860 | 0.45 | 0.19 | -5.509% | 5.509% | site | 0.32 | 1.046
KSA - MBL JCD Opera - S | 2025-07 | KSA | S | 23 | 125 + 125 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 21168 | 49246 | 0.42984 | 34% | 22193 | 0.45066 | 20410 | 0.45 | 0.19 | 4.842% | 4.842% | site | 0.29 | 1
KSA - MBL JCD Opera - S | 2025-08 | KSA | S | 31 | 125 + 125 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 20432 | 57190 | 0.35727 | 29% | 25748 | 0.45022 | 23139 | 0.45 | 0.19 | 26.02% | 26.02% | site | 0.28 | 1.051
KSA - MBL JCD Opera - S | 2025-10 | KSA | S | 31 | 125 + 125 + 220 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 20400 | 40844 | 0.49946 | 30.1% | 18072 | 0.44246 | 18360 | 0.45 | 0.13 | -11.41% | 11.41% | quarter | 0.27 | 0.991
KSA - MBL JCD Opera - S | 2025-11 | KSA | S | 30 | 125 + 125 + 300 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 20620 | 38560 | 0.53475 | 24.7% | 16841 | 0.43675 | 19288 | 0.45 | 0.13 | -18.33% | 18.33% | quarter | 0.27 | 1.081
KSA - MBL JCD Opera - S | 2025-12 | KSA | S | 31 | 125 + 125 + 220 + 220 + 300 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 19130 | 33370 | 0.57327 | 24.2% | 15285 | 0.45805 | 18306 | 0.45 | 0.13 | -20.1% | 20.1% | quarter | 0.23 | 0.999
KSA - MBL JCD Opera - S | 2026-01 | KSA | S | 31 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 25550 | 35058 | 0.72879 | 24.6% | 16652 | 0.47498 | 22322 | 0.45 | 0.19 | -34.83% | 34.83% | quarter | 0.27 | 1.034
KSA - MBL JCD Opera - S | 2026-02 | KSA | S | 28 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 16678 | 30014 | 0.55567 | 27.1% | 14551 | 0.48481 | 15528 | 0.45 | 0.19 | -12.75% | 12.75% | quarter | 0.25 | 0.976
KSA - MBL JCD Opera - S | 2026-03 | KSA | S | 31 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 15126 | 30922 | 0.48917 | 22.1% | 15336 | 0.49596 | 15384 | 0.45 | 0.19 | 1.388% | 1.388% | quarter | 0.24 | 0.958
KSA - MBL JCD Opera - S | 2026-04 | KSA | S | 30 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 16717 | 35830 | 0.46656 | 33.7% | 16875 | 0.47097 | 17177 | 0.45 | 0.24 | 0.9451% | 0.9451% | quarter | 0.28 | 0.978
KSA - MBL JCD Opera - S | 2026-05 | KSA | S | 31 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 20689 | 40510 | 0.51071 | 33.8% | 18895 | 0.46643 | 21363 | 0.45 | 0.24 | -8.671% | 8.671% | quarter | 0.29 | 1
KSA - MBL JCD Opera - S | 2026-06 | KSA | S | 30 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 25040 | 43350 | 0.57762 | 36.7% | 20210 | 0.46621 | 24658 | 0.45 | 0.24 | -19.29% | 19.29% | quarter | 0.3 | 0.982
KSA - MBL JCD Opera - S | 2026-07 | KSA | S | 31 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 25456 | 46975 | 0.54191 | 34.9% | 23731 | 0.50518 | 26114 | 0.45 | 0.12 | -6.776% | 6.776% | quarter | 0.23 | 0.964
KSA - MBL JCD Opera - S | 2026-08 | KSA | S | 31 | 220 + 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 29950 | 54626 | 0.54827 | 31.4% | 26915 | 0.49271 | 28418 | 0.45 | 0.12 | -10.13% | 10.13% | quarter | 0.24 | 1.047
KSA - MBL JCD Opera - S | 2026-09 | KSA | S | 30 | 220 + 300 + 220 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 29867 | 54572 | 0.5473 | 24.2% | 28796 | 0.52767 | 29226 | 0.45 | 0.12 | -3.586% | 3.586% | quarter | 0.21 | 0.996
KSA - MBL Oceanarium - S | 2025-01 | KSA | S | 31 | 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 8750 | 9654 | 0.90636 | 16.3% | 7272 | 0.75326 | 8305 | 0.46 | 0.28 | -16.89% | 16.89% | site | 0.11 | 1.25
KSA - MBL Oceanarium - S | 2025-02 | KSA | S | 27 | 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 8150 | 8803 | 0.92582 | 16.1% | 7806 | 0.88674 | 7808 | 0.46 | 0.28 | -4.221% | 4.221% | site | 0.09 | 1.166
KSA - MBL Oceanarium - S | 2025-03 | KSA | S | 31 | 220 + 125 + 125 + 300 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 9300 | 10835 | 0.85833 | 13% | 9813 | 0.90568 | 8223 | 0.46 | 0.28 | 5.516% | 5.516% | site | 0.08 | 0.97
KSA - MBL Oceanarium - S | 2025-04 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 6250 | 13448 | 0.46475 | 22% | 6691 | 0.49755 | 6775 | 0.46 | 0.28 | 7.056% | 7.056% | site | 0.19 | 1.057
KSA - MBL Oceanarium - S | 2025-06 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 8250 | 17370 | 0.47496 | 17.4% | 7963 | 0.45843 | 7896 | 0.46 | 0.28 | -3.479% | 3.479% | site | 0.23 | 0.978
KSA - MBL Oceanarium - S | 2025-07 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 11879 | 25318 | 0.46919 | 14.8% | 10434 | 0.41212 | 11341 | 0.62 | 0.29 | -12.16% | 12.16% | quarter | 0.34 | 1.006
KSA - MBL Oceanarium - S | 2025-08 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 13321 | 29277 | 0.455 | 12.2% | 11836 | 0.40428 | 12070 | 0.62 | 0.29 | -11.15% | 11.15% | quarter | 0.37 | 0.995
KSA - MBL Oceanarium - S | 2025-09 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 10150 | 27882 | 0.36403 | 12% | 11256 | 0.4037 | 11256 | 0.62 | 0.29 | 10.9% | 10.9% | quarter | 0.37 | 1.077
KSA - MBL Oceanarium - S | 2025-10 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7550 | 19888 | 0.37963 | 21.8% | 8742 | 0.43956 | 8639 | 0.45 | 0.15 | 15.79% | 15.79% | quarter | 0.26 | 0.915
KSA - MBL Oceanarium - S | 2025-11 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 8409 | 17741 | 0.47399 | 20.9% | 8004 | 0.45116 | 7967 | 0.45 | 0.15 | -4.816% | 4.816% | quarter | 0.24 | 1.021
KSA - MBL Oceanarium - S | 2025-12 | KSA | S | 31 | 125 + 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7276 | 16588 | 0.43863 | 13.3% | 7684 | 0.46323 | 7685 | 0.45 | 0.15 | 5.607% | 5.607% | quarter | 0.22 | 1.059
KSA - MBL Oceanarium - S | 2026-01 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7915 | 16024 | 0.49395 | 21.9% | 7425 | 0.46337 | 7432 | 0.45 | 0.2 | -6.191% | 6.191% | quarter | 0.22 | 1.034
KSA - MBL Oceanarium - S | 2026-02 | KSA | S | 28 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 6009 | 14217 | 0.42266 | 22.1% | 6684 | 0.47014 | 6695 | 0.45 | 0.2 | 11.23% | 11.23% | quarter | 0.21 | 0.976
KSA - MBL Oceanarium - S | 2026-03 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 6202 | 13250 | 0.46808 | 13.6% | 6607 | 0.49864 | 6642 | 0.45 | 0.2 | 6.53% | 6.53% | quarter | 0.18 | 0.986
KSA - MBL Oceanarium - S | 2026-06 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7807 | 19750 | 0.39529 | 29.2% | 8517 | 0.43124 | 8557 | 0.45 | 0.26 | 9.094% | 9.094% | quarter | 0.27 | 0.982
KSA - MBL Oceanarium - S | 2026-07 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 8613 | 22820 | 0.37743 | 28.3% | 9553 | 0.41862 | 9573 | 0.51 | 0.29 | 10.91% | 10.91% | quarter | 0.31 | 0.94
KSA - MBL Oceanarium - S | 2026-08 | KSA | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 11088 | 26256 | 0.4223 | 26.2% | 10681 | 0.4068 | 10657 | 0.51 | 0.29 | -3.671% | 3.671% | quarter | 0.35 | 1.008
KSA - MBL Oceanarium - S | 2026-09 | KSA | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 9212 | 24382 | 0.37782 | 23.7% | 9992 | 0.40981 | 9980 | 0.51 | 0.29 | 8.467% | 8.467% | quarter | 0.33 | 0.989
KSA - MBL Opera - S | 2025-01 | KSA | S | 27 | 125 + 125 + 125 | JCB 448 (125 kVA) | 11732 | 15612 | 0.75147 | 13% | 6635 | 0.42499 | 6687 | 0.55 | 0.15 | -43.45% | 43.45% | site | 0.25 | 1.065
KSA - MBL Opera - S | 2025-02 | KSA | S | 25 | 125 + 125 + 125 | JCB 448 (125 kVA) | 6800 | 14450 | 0.47059 | 13.3% | 6174 | 0.42727 | 6176 | 0.55 | 0.15 | -9.206% | 9.206% | site | 0.25 | 1.164
KSA - MBL Opera - S | 2025-03 | KSA | S | 31 | 125 + 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 10333 | 16762 | 0.61645 | 12% | 7336 | 0.43766 | 7574 | 0.55 | 0.15 | -29% | 29% | site | 0.23 | 1.003
KSA - MBL Opera - S | 2025-04 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 8224 | 20663 | 0.39801 | 18.6% | 8357 | 0.40444 | 8382 | 0.55 | 0.24 | 1.617% | 1.617% | site | 0.29 | 1.085
KSA - MBL Opera - S | 2025-06 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 8710 | 20042 | 0.43459 | 21% | 8134 | 0.40585 | 8150 | 0.55 | 0.24 | -6.613% | 6.613% | site | 0.28 | 1.005
KSA - MBL Opera - S | 2025-08 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 11760 | 27946 | 0.42081 | 14% | 10498 | 0.37565 | 10621 | 0.6 | 0.31 | -10.73% | 10.73% | quarter | 0.37 | 0.995
KSA - MBL Opera - S | 2025-09 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 10440 | 25164 | 0.41488 | 14.7% | 9600 | 0.3815 | 9671 | 0.6 | 0.31 | -8.046% | 8.046% | quarter | 0.35 | 1.031
KSA - MBL Opera - S | 2025-10 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 9338 | 21450 | 0.43534 | 23.1% | 8567 | 0.39939 | 8588 | 0.55 | 0.24 | -8.257% | 8.257% | site | 0.3 | 0.997
KSA - MBL Opera - S | 2025-11 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 8812 | 20394 | 0.43209 | 22.6% | 8237 | 0.40389 | 8234 | 0.55 | 0.24 | -6.525% | 6.525% | site | 0.29 | 1.035
KSA - MBL Opera - S | 2025-12 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 7325 | 16577 | 0.44188 | 18.7% | 7372 | 0.44471 | 7374 | 0.55 | 0.24 | 0.6416% | 0.6416% | site | 0.22 | 1.059
KSA - MBL Opera - S | 2026-01 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 7285 | 15226 | 0.47846 | 25.2% | 7003 | 0.45994 | 7022 | 0.45 | 0.24 | -3.871% | 3.871% | quarter | 0.21 | 1.018
KSA - MBL Opera - S | 2026-02 | KSA | S | 28 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 6187 | 12952 | 0.47769 | 28% | 6122 | 0.47267 | 6124 | 0.45 | 0.24 | -1.051% | 1.051% | quarter | 0.19 | 0.976
KSA - MBL Opera - S | 2026-03 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 5646 | 14766 | 0.38236 | 23.7% | 6781 | 0.45923 | 6798 | 0.45 | 0.24 | 20.1% | 20.1% | quarter | 0.21 | 1.004
KSA - MBL Opera - S | 2026-04 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 8970 | 18926 | 0.47395 | 28.4% | 7941 | 0.41958 | 7905 | 0.45 | 0.21 | -11.47% | 11.47% | quarter | 0.26 | 0.982
KSA - MBL Opera - S | 2026-07 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 8464 | 21365 | 0.39616 | 30.8% | 8632 | 0.40403 | 8635 | 0.59 | 0.3 | 1.985% | 1.985% | quarter | 0.29 | 0.952
KSA - MBL Opera - S | 2026-08 | KSA | S | 31 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 11127 | 25413 | 0.43785 | 27.5% | 9747 | 0.38354 | 9775 | 0.59 | 0.3 | -12.4% | 12.4% | quarter | 0.34 | 1.01
KSA - MBL Opera - S | 2026-09 | KSA | S | 30 | 125 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 11352 | 26044 | 0.43588 | 22.1% | 9831 | 0.37748 | 9887 | 0.59 | 0.3 | -13.4% | 13.4% | quarter | 0.36 | 0.986
KSA - Namareq KAEC - C | 2025-05 | KSA | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 241841 | 656539 | 0.36836 | 0% | 206844 | 0.31505 | 207243 | 0.61 | 0.41 | -14.47% | 14.47% | quarter | 0.45 | 0.969
KSA - Namareq KAEC - C | 2025-06 | KSA | C | 30 | 1250 + 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 232117 | 686189 | 0.33827 | 0% | 214192 | 0.31215 | 216119 | 0.61 | 0.41 | -7.722% | 7.722% | quarter | 0.48 | 0.973
KSA - Namareq KAEC - C | 2025-09 | KSA | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 219144 | 625440 | 0.35038 | 19.1% | 195471 | 0.31253 | 197003 | 0.67 | 0.4 | -10.8% | 10.8% | quarter | 0.49 | 0.939
KSA - Namareq KAEC - C | 2025-10 | KSA | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 168662 | 509359 | 0.33113 | 21% | 160084 | 0.31429 | 161483 | 0.74 | 0.38 | -5.086% | 5.086% | quarter | 0.47 | 0.93
KSA - Namareq KAEC - C | 2025-11 | KSA | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 150989 | 466397 | 0.32373 | 20% | 147587 | 0.31644 | 148935 | 0.74 | 0.38 | -2.253% | 2.253% | quarter | 0.46 | 0.944
KSA - Namareq KAEC - C | 2025-12 | KSA | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 125344 | 376529 | 0.33289 | 20.3% | 119941 | 0.31854 | 122522 | 0.74 | 0.38 | -4.311% | 4.311% | quarter | 0.46 | 0.895
KSA - Namareq KAEC - C | 2026-01 | KSA | C | 31 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 119816 | 366010 | 0.32736 | 21.2% | 117043 | 0.31978 | 118307 | 0.76 | 0.38 | -2.314% | 2.314% | quarter | 0.46 | 0.921
KSA - Namareq KAEC - C | 2026-02 | KSA | C | 28 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 111446 | 340242 | 0.32755 | 25.1% | 108435 | 0.3187 | 109887 | 0.76 | 0.38 | -2.702% | 2.702% | quarter | 0.47 | 0.924
KSA - Namareq KAEC - C | 2026-03 | KSA | C | 31 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 108977 | 325390 | 0.33491 | 29.4% | 105411 | 0.32395 | 106831 | 0.76 | 0.38 | -3.272% | 3.272% | quarter | 0.43 | 0.899
KSA - Namareq KAEC - C | 2026-04 | KSA | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 126721 | 364608 | 0.34755 | 28.7% | 118526 | 0.32508 | 119650 | 0.73 | 0.34 | -6.467% | 6.467% | quarter | 0.41 | 0.916
KSA - Namareq KAEC - C | 2026-05 | KSA | C | 31 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 130620 | 389282 | 0.33554 | 30.8% | 126369 | 0.32462 | 129038 | 0.73 | 0.34 | -3.254% | 3.254% | quarter | 0.42 | 0.91
KSA - Namareq KAEC - C | 2026-06 | KSA | C | 30 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 142215 | 429153 | 0.33139 | 28.7% | 138131 | 0.32187 | 139719 | 0.73 | 0.34 | -2.872% | 2.872% | quarter | 0.42 | 0.917
KSA - Namareq KAEC - C | 2026-07 | KSA | C | 31 | 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 166628 | 520706 | 0.32 | 25.2% | 164693 | 0.31629 | 165642 | 0.69 | 0.38 | -1.161% | 1.161% | quarter | 0.44 | 0.926
KSA - Namareq KAEC - C | 2026-08 | KSA | C | 31 | 1250 + 1250 + 1250 + 1125 | Cummins KTA50 (1250 kVA), unlisted 1000–1250 kVA | 174496 | 544630 | 0.32039 | 23% | 171170 | 0.31429 | 172948 | 0.69 | 0.38 | -1.906% | 1.906% | quarter | 0.46 | 0.935
KSA - Namareq KAEC - C | 2026-09 | KSA | C | 30 | 1250 + 1125 + 1250 + 1250 | Cummins KTA50 (1250 kVA), unlisted 1000–1250 kVA | 187753 | 572258 | 0.32809 | 20.6% | 178565 | 0.31204 | 180275 | 0.69 | 0.38 | -4.894% | 4.894% | quarter | 0.49 | 0.962
KSA - Namariq Jizan - C | 2025-09 | KSA | C | 30 | 1000 + 1000 + 1000 + 500 + 500 + 1000 + 500 + 500 + 500 + 500 + 1000 + 500 + 500 + 500 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 345721 | 1100755 | 0.31408 | 1.5% | 345817 | 0.31416 | 351258 | 0.45 | 0.34 | 0.02777% | 0.02777% | quarter | 0.39 | 1.03
KSA - Namariq Jizan - C | 2025-10 | KSA | C | 31 | 1000 + 1000 + 1000 + 1000 + 500 + 1000 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 271276 | 888791 | 0.30522 | 4.8% | 273392 | 0.3076 | 276311 | 0.45 | 0.32 | 0.78% | 0.78% | quarter | 0.38 | 1
KSA - Namariq Jizan - C | 2025-11 | KSA | C | 30 | 1000 + 1000 + 1000 + 500 + 1000 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 242148 | 769955 | 0.3145 | 4.8% | 237539 | 0.30851 | 240012 | 0.45 | 0.32 | -1.903% | 1.903% | quarter | 0.37 | 0.963
KSA - Namariq Jizan - C | 2025-12 | KSA | C | 31 | 1000 + 500 + 1000 + 1000 + 500 + 500 + 500 + 1000 + 500 + 500 + 500 + 1000 + 500 + 500 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 216641 | 650715 | 0.33293 | 4.7% | 203394 | 0.31257 | 207470 | 0.45 | 0.32 | -6.115% | 6.115% | quarter | 0.37 | 0.985
KSA - Namariq Jizan - C | 2026-02 | KSA | C | 28 | 500 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 1000 + 1000 + 1000 + 1000 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 229314 | 698776 | 0.32817 | 4.3% | 231963 | 0.33196 | 234543 | 0.52 | 0.36 | 1.155% | 1.155% | quarter | 0.43 | 1.037
KSA - Namariq Jizan - C | 2026-03 | KSA | C | 31 | 500 + 500 + 500 + 500 + 500 + 500 + 500 + 1000 + 500 + 500 + 1000 + 1000 + 1000 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 274224 | 877992 | 0.31233 | 5.3% | 288599 | 0.3287 | 286258 | 0.52 | 0.36 | 5.242% | 5.242% | quarter | 0.44 | 1.195
KSA - Namariq Jizan - C | 2026-04 | KSA | C | 30 | 500 + 500 + 500 + 500 + 500 + 500 + 500 + 1000 + 500 + 1000 + 1000 + 1000 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 307285 | 973375 | 0.31569 | 5.2% | 318867 | 0.32759 | 319510 | 0.53 | 0.37 | 3.769% | 3.769% | quarter | 0.45 | 0.985
KSA - Namariq Jizan - C | 2026-05 | KSA | C | 31 | 500 + 1000 + 1000 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 1000 + 1000 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 310553 | 1026543 | 0.30252 | 5.4% | 326026 | 0.3176 | 331855 | 0.53 | 0.37 | 4.982% | 4.982% | quarter | 0.45 | 0.981
KSA - Namariq Jizan - C | 2026-06 | KSA | C | 30 | 1000 + 1000 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 500 + 1000 + 1000 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 310703 | 1041104 | 0.29844 | 4.9% | 332100 | 0.31899 | 336098 | 0.53 | 0.37 | 6.887% | 6.887% | quarter | 0.45 | 0.991
KSA - Namariq Jizan - C | 2026-07 | KSA | C | 31 | 1000 + 1000 + 500 + 500 + 500 + 500 + 500 + 1000 + 500 + 500 + 500 + 500 + 1000 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 312987 | 1044074 | 0.29977 | 4.7% | 331614 | 0.31762 | 336823 | 0.62 | 0.49 | 5.951% | 5.951% | quarter | 0.55 | 0.975
KSA - Namariq Jizan - C | 2026-08 | KSA | C | 31 | 500 + 1000 + 500 + 500 + 1000 + 500 + 500 + 1000 + 500 + 500 + 500 + 500 + 1000 + 500 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 471565 | 1585106 | 0.2975 | 3.1% | 504671 | 0.31838 | 504335 | 0.62 | 0.49 | 7.02% | 7.02% | quarter | 0.55 | 1.049
KSA - Namariq Jizan - C | 2026-09 | KSA | C | 30 | 500 + 500 + 1000 + 500 + 1000 + 500 + 500 + 500 + 1000 + 500 + 500 + 500 + 1000 | Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 478666 | 1621491 | 0.2952 | 2.8% | 504900 | 0.31138 | 506917 | 0.62 | 0.49 | 5.481% | 5.481% | quarter | 0.55 | 1.102
KSA - Ramz Al Akhwa - C | 2025-09 | KSA | C | 30 | 500 + 500 + 500 | unlisted 500 kVA | 75176 | 266587 | 0.28199 | 14.5% | 76952 | 0.28866 | 76571 | 0.72 | 0.45 | 2.362% | 2.362% | quarter | 0.5 | 1.086
KSA - Ramz Al Akhwa - C | 2025-10 | KSA | C | 31 | 500 + 500 + 500 | unlisted 500 kVA | 61996 | 198579 | 0.3122 | 18.7% | 59108 | 0.29765 | 58303 | 0.71 | 0.36 | -4.658% | 4.658% | quarter | 0.44 | 1.125
KSA - Ramz Al Akhwa - C | 2025-11 | KSA | C | 30 | 500 + 500 + 500 + 500 | unlisted 500 kVA | 34474 | 113563 | 0.30357 | 19.1% | 36098 | 0.31787 | 36123 | 0.71 | 0.36 | 4.711% | 4.711% | quarter | 0.39 | 1.046
KSA - Ramz Al Akhwa - C | 2025-12 | KSA | C | 31 | 500 + 500 + 500 | unlisted 500 kVA | 39411 | 129914 | 0.30336 | 13.9% | 40785 | 0.31394 | 40743 | 0.71 | 0.36 | 3.486% | 3.486% | quarter | 0.39 | 1.07
KSA - Ramz Al Akhwa - C | 2026-01 | KSA | C | 31 | 500 + 500 | unlisted 500 kVA | 44184 | 149432 | 0.29568 | 12% | 46575 | 0.31168 | 46595 | 0.71 | 0.35 | 5.411% | 5.411% | quarter | 0.39 | 1
KSA - Ramz Al Akhwa - C | 2026-02 | KSA | C | 28 | 500 + 500 | unlisted 500 kVA | 31240 | 98664 | 0.31663 | 19.3% | 32526 | 0.32966 | 32659 | 0.71 | 0.35 | 4.117% | 4.117% | quarter | 0.35 | 1.023
KSA - Ramz Al Akhwa - C | 2026-03 | KSA | C | 31 | 500 + 500 | unlisted 500 kVA | 22378 | 66049 | 0.33881 | 20% | 26612 | 0.40291 | 26657 | 0.71 | 0.35 | 18.92% | 18.92% | quarter | 0.22 | 1.005
KSA - Ramz Al Akhwa - C | 2026-04 | KSA | C | 30 | 500 + 500 | unlisted 500 kVA | 24003 | 63610 | 0.37735 | 19.9% | 25898 | 0.40714 | 26155 | 0.72 | 0.36 | 7.895% | 7.895% | quarter | 0.22 | 1.009
KSA - Ramz Al Akhwa - C | 2026-05 | KSA | C | 31 | 500 + 500 | unlisted 500 kVA | 52510 | 171945 | 0.30539 | 21.5% | 52575 | 0.30577 | 52847 | 0.72 | 0.36 | 0.1238% | 0.1238% | quarter | 0.39 | 1.084
KSA - Ramz Al Akhwa - C | 2026-06 | KSA | C | 30 | 500 + 500 | unlisted 500 kVA | 64358 | 217900 | 0.29536 | 20.8% | 63297 | 0.29049 | 61506 | 0.72 | 0.36 | -1.649% | 1.649% | quarter | 0.51 | 1.25
KSA - Ramz Al Akhwa - C | 2026-07 | KSA | C | 31 | 500 + 500 | unlisted 500 kVA | 28651 | 81347 | 0.35221 | 26.1% | 30041 | 0.36929 | 28382 | 0.57 | 0.34 | 4.851% | 4.851% | quarter | 0.24 | 1.25
KSA - Ramz Al Akhwa - C | 2026-08 | KSA | C | 31 | 300 + 500 + 500 + 300 | JD 6090 (300 kVA), unlisted 500 kVA | 15209 | 29151 | 0.52173 | 33.7% | 15937 | 0.54671 | 16412 | 0.57 | 0.34 | 4.787% | 4.787% | quarter | 0.2 | 1.25
KSA - Ramz Al Akhwa - C | 2026-09 | KSA | C | 30 | 300 + 300 | JD 6090 (300 kVA) | 14732 | 27465 | 0.53639 | 29.8% | 15219 | 0.55412 | 15126 | 0.57 | 0.34 | 3.306% | 3.306% | quarter | 0.19 | 1.25
KSA - Sprint - I | 2025-01 | KSA | I | 26 | 125 + 125 + 60 | unlisted ≤125 kVA | 4410 | 4173 | 1.0568 | 5.2% | 2927 | 0.70141 | 2884 | 0.48 | 0.24 | -33.63% | 33.63% | site | 0.07 | 1.236
KSA - Sprint - I | 2025-02 | KSA | I | 25 | 60 + 125 | unlisted ≤125 kVA | 3250 | 3798 | 0.85571 | 1.3% | 1991 | 0.52422 | 2290 | 0.48 | 0.24 | -38.74% | 38.74% | site | 0.14 | 1.162
KSA - Sprint - I | 2025-03 | KSA | I | 31 | 60 + 125 | unlisted ≤125 kVA | 3927 | 4331 | 0.90672 | 2% | 2377 | 0.54883 | 2671 | 0.48 | 0.24 | -39.47% | 39.47% | site | 0.12 | 1.038
KSA - Sprint - I | 2025-04 | KSA | I | 30 | 60 + 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 5807 | 10501 | 0.55299 | 16.1% | 4767 | 0.45396 | 4983 | 0.48 | 0.24 | -17.91% | 17.91% | site | 0.23 | 1.054
KSA - Sprint - I | 2025-06 | KSA | I | 29 | 125 + 125 | JCB 448 (125 kVA), unlisted ≤125 kVA | 5935 | 16608 | 0.35736 | 18.1% | 7508 | 0.45207 | 7244 | 0.48 | 0.24 | 26.5% | 26.5% | site | 0.2 | 1.25
KSA - Sprint - I | 2025-08 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 10959 | 20227 | 0.5418 | 13.2% | 10456 | 0.51693 | 9828 | 0.45 | 0.05 | -4.59% | 4.59% | quarter | 0.17 | 1.037
KSA - Sprint - I | 2025-09 | KSA | I | 30 | 125 + 125 + 125 | JCB 448 (125 kVA) | 9031 | 15855 | 0.5696 | 13.7% | 8041 | 0.50716 | 8213 | 0.45 | 0.05 | -10.96% | 10.96% | quarter | 0.18 | 0.98
KSA - Sprint - I | 2025-10 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 6373 | 11141 | 0.57203 | 18% | 5939 | 0.53308 | 5944 | 0.48 | 0.24 | -6.81% | 6.81% | site | 0.15 | 1.012
KSA - Sprint - I | 2025-11 | KSA | I | 30 | 125 + 125 | JCB 448 (125 kVA) | 5857 | 7626 | 0.76803 | 13.1% | 4932 | 0.64673 | 4937 | 0.48 | 0.24 | -15.79% | 15.79% | site | 0.11 | 1.061
KSA - Sprint - I | 2025-12 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 4819 | 4730 | 1.0188 | 2.3% | 4194 | 0.88668 | 4136 | 0.48 | 0.24 | -12.97% | 12.97% | site | 0.07 | 0.98
KSA - Sprint - I | 2026-01 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 5258 | 3990 | 1.3178 | 2.1% | 3966 | 0.99398 | 3957 | 0.48 | 0.24 | -24.57% | 24.57% | site | 0.06 | 1.048
KSA - Sprint - I | 2026-02 | KSA | I | 28 | 125 + 125 | JCB 448 (125 kVA) | 4426 | 3511 | 1.2606 | 3.1% | 3525 | 1.004 | 3523 | 0.48 | 0.24 | -20.36% | 20.36% | site | 0.05 | 1.002
KSA - Sprint - I | 2026-03 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 5091 | 4423 | 1.151 | 4.4% | 4057 | 0.91725 | 4069 | 0.48 | 0.24 | -20.31% | 20.31% | site | 0.06 | 1.03
KSA - Sprint - I | 2026-04 | KSA | I | 30 | 125 + 125 | JCB 448 (125 kVA) | 5583 | 6683 | 0.8354 | 13.4% | 4549 | 0.68068 | 4550 | 0.47 | 0.24 | -18.52% | 18.52% | quarter | 0.1 | 1.018
KSA - Sprint - I | 2026-05 | KSA | I | 31 | 125 + 125 | JCB 448 (125 kVA) | 6744 | 11848 | 0.56921 | 18.5% | 6154 | 0.51941 | 6314 | 0.47 | 0.24 | -8.749% | 8.749% | quarter | 0.16 | 1.063
KSA - Sprint - I | 2026-06 | KSA | I | 30 | 125 + 125 + 125 | JCB 448 (125 kVA) | 8274 | 16326 | 0.5068 | 17.6% | 7715 | 0.47256 | 7846 | 0.47 | 0.24 | -6.756% | 6.756% | quarter | 0.19 | 1.048
KSA - Sprint - I | 2026-07 | KSA | I | 31 | 125 + 125 + 125 | JCB 448 (125 kVA) | 8423 | 18278 | 0.46083 | 15.8% | 8497 | 0.46488 | 8274 | 0.48 | 0.25 | 0.8785% | 0.8785% | quarter | 0.19 | 1.088
UAE - AL Saida Fujeirah - C | 2025-03 | UAE | C | 31 | 125 + 250 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA) | 11036 | 24550 | 0.44953 | 0% | 9986 | 0.40676 | 9686 | 0.45 | 0.3 | -9.514% | 9.514% | quarter | 0.26 | 1.114
UAE - AL Saida Fujeirah - C | 2025-05 | UAE | C | 31 | 125 + 125 + 125 | JCB 448 (125 kVA) | 13951 | 40971 | 0.34051 | 0% | 14824 | 0.36182 | 16038 | 0.56 | 0.28 | 6.258% | 6.258% | quarter | 0.41 | 0.982
UAE - Al Dar - S | 2025-01 | UAE | S | 20 | 125 + 350 + 300 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 8426 | 24856 | 0.33899 | 16.1% | 9524 | 0.38317 | 9903 | 0.48 | 0.13 | 13.03% | 13.03% | quarter | 0.32 | 1.024
UAE - Al Dar - S | 2025-02 | UAE | S | 25 | 125 + 350 + 300 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 10090 | 25969 | 0.38854 | 17.8% | 12268 | 0.47241 | 11825 | 0.48 | 0.13 | 21.59% | 21.59% | quarter | 0.26 | 1.242
UAE - Al Dar - S | 2025-03 | UAE | S | 31 | 125 + 350 + 300 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 9466 | 24131 | 0.39228 | 25% | 9944 | 0.41208 | 10339 | 0.48 | 0.13 | 5.05% | 5.05% | quarter | 0.29 | 0.954
UAE - Al Dar - S | 2025-09 | UAE | S | 30 | 250 + 125 + 300 + 220 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 25274 | 70621 | 0.35788 | 16.2% | 22781 | 0.32258 | 24523 | 0.55 | 0.36 | -9.864% | 9.864% | quarter | 0.42 | 0.968
UAE - Al Dar - S | 2025-10 | UAE | S | 31 | 300 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 27787 | 68542 | 0.4054 | 15.4% | 27553 | 0.40199 | 26651 | 0.5 | 0.32 | -0.8421% | 0.8421% | quarter | 0.36 | 1.022
UAE - Al Dar - S | 2025-11 | UAE | S | 30 | 220 + 250 + 125 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 18997 | 43890 | 0.43283 | 18.9% | 18280 | 0.4165 | 17643 | 0.5 | 0.32 | -3.774% | 3.774% | quarter | 0.3 | 1.029
UAE - Al Dar - S | 2025-12 | UAE | S | 31 | 250 + 220 + 125 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA) | 12633 | 28401 | 0.44481 | 23.1% | 11658 | 0.41048 | 12407 | 0.5 | 0.32 | -7.718% | 7.718% | quarter | 0.19 | 0.999
UAE - Al Dar - S | 2026-01 | UAE | S | 31 | 250 + 220 + 125 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA) | 11012 | 22525 | 0.48888 | 27.2% | 10282 | 0.45647 | 10346 | 0.56 | 0.23 | -6.629% | 6.629% | quarter | 0.15 | 1.008
UAE - Al Dar - S | 2026-02 | UAE | S | 28 | 250 + 125 + 220 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA) | 9334 | 25481 | 0.36631 | 29.2% | 10424 | 0.40909 | 10004 | 0.56 | 0.23 | 11.68% | 11.68% | quarter | 0.19 | 0.999
UAE - Al Dar - S | 2026-04 | UAE | S | 30 | 220 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 15083 | 36888 | 0.40889 | 26.1% | 18160 | 0.4923 | 18331 | 0.57 | 0.27 | 20.4% | 20.4% | quarter | 0.28 | 0.967
UAE - Al Dar - S | 2026-05 | UAE | S | 31 | 220 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 23326 | 60115 | 0.38802 | 23.5% | 26507 | 0.44094 | 26374 | 0.57 | 0.27 | 13.64% | 13.64% | quarter | 0.38 | 1.031
UAE - Al Dar - S | 2026-06 | UAE | S | 30 | 250 + 220 + 220 + 125 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 20669 | 67400 | 0.30666 | 20% | 25150 | 0.37315 | 21759 | 0.57 | 0.27 | 21.68% | 21.68% | quarter | 0.37 | 1.239
UAE - Al Dar - S | 2026-07 | UAE | S | 31 | 250 + 220 + 220 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 26318 | 82312 | 0.31973 | 16.6% | 31240 | 0.37953 | 27629 | 0.56 | 0.27 | 18.7% | 18.7% | quarter | 0.37 | 1.25
UAE - Al Dar - S | 2026-08 | UAE | S | 31 | 220 + 220 + 250 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 35283 | 93227 | 0.37846 | 13.6% | 39542 | 0.42415 | 37738 | 0.56 | 0.27 | 12.07% | 12.07% | quarter | 0.38 | 1.011
UAE - Al Dar - S | 2026-09 | UAE | S | 30 | 300 + 220 + 220 + 250 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 28121 | 78435 | 0.35853 | 15.1% | 26537 | 0.33833 | 29100 | 0.56 | 0.27 | -5.633% | 5.633% | quarter | 0.38 | 1.027
UAE - Arabian Industries - C | 2025-05 | UAE | C | 27 | 500 + 800 + 350 + 500 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 31845 | 94714 | 0.33622 | 30% | 29894 | 0.31562 | 30212 | 0.61 | 0.23 | -6.127% | 6.127% | quarter | 0.34 | 1.178
UAE - Arabian Industries - C | 2025-06 | UAE | C | 30 | 500 + 350 + 800 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 31162 | 95947 | 0.32478 | 31.6% | 28301 | 0.29496 | 28914 | 0.61 | 0.23 | -9.181% | 9.181% | quarter | 0.32 | 0.989
UAE - Arabian Industries - C | 2025-07 | UAE | C | 30 | 500 + 800 + 350 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 39209 | 120423 | 0.32559 | 29.8% | 34094 | 0.28312 | 33324 | 0.62 | 0.34 | -13.05% | 13.05% | quarter | 0.4 | 1.25
UAE - Arabian Industries - C | 2025-08 | UAE | C | 31 | 500 + 350 + 800 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 38641 | 127344 | 0.30344 | 29% | 35954 | 0.28234 | 35734 | 0.62 | 0.34 | -6.954% | 6.954% | quarter | 0.39 | 1.075
UAE - Arabian Industries - C | 2025-09 | UAE | C | 30 | 500 + 350 + 800 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 33193 | 105289 | 0.31526 | 27.2% | 30206 | 0.28689 | 30939 | 0.62 | 0.34 | -8.999% | 8.999% | quarter | 0.35 | 0.959
UAE - Arabian Industries - C | 2025-10 | UAE | C | 31 | 350 + 800 + 500 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 27016 | 89418 | 0.30213 | 25.2% | 29704 | 0.33219 | 29448 | 0.61 | 0.31 | 9.95% | 9.95% | quarter | 0.38 | 1.04
UAE - Arabian Industries - C | 2025-11 | UAE | C | 30 | 350 + 500 + 800 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), unlisted 500 kVA | 22812 | 65720 | 0.34711 | 19.1% | 22431 | 0.34131 | 22519 | 0.61 | 0.31 | -1.67% | 1.67% | quarter | 0.33 | 1.001
UAE - Arabian Industries - C | 2025-12 | UAE | C | 31 | 350 + 300 + 500 + 800 + 500 + 500 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 20535 | 61063 | 0.33629 | 12.5% | 21457 | 0.35139 | 22785 | 0.61 | 0.31 | 4.49% | 4.49% | quarter | 0.3 | 1.01
UAE - Arabian Industries - C | 2026-01 | UAE | C | 31 | 500 + 300 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 19650 | 50353 | 0.39024 | 18.2% | 20254 | 0.40224 | 21205 | 0.45 | 0.16 | 3.074% | 3.074% | quarter | 0.17 | 0.989
UAE - Arabian Industries - C | 2026-02 | UAE | C | 28 | 500 + 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 20598 | 51698 | 0.39843 | 19.2% | 19555 | 0.37825 | 19426 | 0.45 | 0.16 | -5.064% | 5.064% | quarter | 0.19 | 1.006
UAE - Arabian Industries - C | 2026-03 | UAE | C | 31 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 18879 | 63449 | 0.29755 | 18.9% | 22145 | 0.34902 | 21389 | 0.45 | 0.16 | 17.3% | 17.3% | quarter | 0.31 | 1.13
UAE - Arabian Industries - C | 2026-04 | UAE | C | 30 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 19489 | 65005 | 0.29981 | 23.1% | 21453 | 0.33002 | 21327 | 0.71 | 0.29 | 10.08% | 10.08% | quarter | 0.38 | 1.25
UAE - Arabian Industries - C | 2026-05 | UAE | C | 31 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 25340 | 86790 | 0.29197 | 31.2% | 27832 | 0.32068 | 27523 | 0.71 | 0.29 | 9.834% | 9.834% | quarter | 0.42 | 1.187
UAE - Arabian Industries - C | 2026-06 | UAE | C | 30 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 27805 | 93187 | 0.29838 | 32.5% | 30023 | 0.32218 | 30157 | 0.71 | 0.29 | 7.977% | 7.977% | quarter | 0.41 | 0.982
UAE - Arabian Industries - C | 2026-07 | UAE | C | 31 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 32259 | 109001 | 0.29595 | 32.5% | 35420 | 0.32495 | 35007 | 0.54 | 0.28 | 9.799% | 9.799% | quarter | 0.34 | 0.992
UAE - Arabian Industries - C | 2026-08 | UAE | C | 31 | 500 + 350 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 41258 | 128349 | 0.32145 | 30.5% | 40897 | 0.31864 | 41494 | 0.54 | 0.28 | -0.875% | 0.875% | quarter | 0.34 | 0.991
UAE - Arabian Industries - C | 2026-09 | UAE | C | 30 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA), unlisted 500 kVA | 36607 | 112027 | 0.32677 | 30.5% | 37145 | 0.33157 | 37936 | 0.54 | 0.28 | 1.47% | 1.47% | quarter | 0.35 | 0.998
UAE - EAST VILLE Fujeirah - C | 2025-01 | UAE | C | 31 | 800 + 300 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 47013 | 152244 | 0.3088 | 0% | 46213 | 0.30355 | 46073 | 0.45 | 0.21 | -1.702% | 1.702% | quarter | 0.3 | 1
UAE - EAST VILLE Fujeirah - C | 2025-02 | UAE | C | 28 | 800 + 300 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 45978 | 148924 | 0.30873 | 0% | 45766 | 0.30731 | 43662 | 0.45 | 0.21 | -0.4611% | 0.4611% | quarter | 0.3 | 1.029
UAE - EAST VILLE Fujeirah - C | 2025-03 | UAE | C | 31 | 800 + 1000 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 52799 | 174966 | 0.30177 | 0% | 51322 | 0.29333 | 50870 | 0.45 | 0.21 | -2.797% | 2.797% | quarter | 0.29 | 1.004
UAE - EAST VILLE Fujeirah - C | 2025-05 | UAE | C | 31 | 800 + 1000 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 86812 | 289240 | 0.30014 | 0% | 81802 | 0.28282 | 83252 | 0.65 | 0.34 | -5.771% | 5.771% | quarter | 0.44 | 0.989
UAE - EAST VILLE Fujeirah - C | 2025-06 | UAE | C | 30 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 112519 | 368696 | 0.30518 | 0% | 100673 | 0.27305 | 101918 | 0.65 | 0.34 | -10.53% | 10.53% | quarter | 0.46 | 1.063
UAE - EAST VILLE Fujeirah - C | 2025-07 | UAE | C | 30 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 99148 | 344783 | 0.28757 | 0% | 94556 | 0.27425 | 92936 | 0.65 | 0.34 | -4.631% | 4.631% | quarter | 0.43 | 1.126
UAE - EAST VILLE Fujeirah - C | 2025-08 | UAE | C | 31 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 103924 | 348312 | 0.29836 | 0% | 94929 | 0.27254 | 94170 | 0.65 | 0.34 | -8.655% | 8.655% | quarter | 0.45 | 1.039
UAE - EAST VILLE Fujeirah - C | 2025-09 | UAE | C | 30 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 92607 | 314631 | 0.29434 | 0% | 85044 | 0.2703 | 85495 | 0.65 | 0.34 | -8.167% | 8.167% | quarter | 0.47 | 0.969
UAE - EAST VILLE Fujeirah - C | 2025-10 | UAE | C | 31 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 81274 | 267200 | 0.30417 | 0% | 75524 | 0.28265 | 74059 | 0.45 | 0.31 | -7.075% | 7.075% | quarter | 0.32 | 1.036
UAE - EAST VILLE Fujeirah - C | 2025-11 | UAE | C | 30 | 1000 + 800 + 300 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 46740 | 134996 | 0.34623 | 3.2% | 40726 | 0.30168 | 40163 | 0.45 | 0.31 | -12.87% | 12.87% | quarter | 0.22 | 1.008
UAE - EAST VILLE Fujeirah - C | 2025-12 | UAE | C | 31 | 800 + 350 + 1000 + 300 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), JD 6090 (300 kVA) | 31300 | 80176 | 0.39039 | 14.6% | 25960 | 0.32379 | 25926 | 0.45 | 0.31 | -17.06% | 17.06% | quarter | 0.17 | 1.042
UAE - EAST VILLE Fujeirah - C | 2026-01 | UAE | C | 31 | 350 + 800 + 1000 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 20410 | 58205 | 0.35066 | 17.5% | 19363 | 0.33267 | 18990 | 0.49 | 0.3 | -5.13% | 5.13% | quarter | 0.32 | 1.25
UAE - EAST VILLE Fujeirah - C | 2026-02 | UAE | C | 28 | 800 + 350 + 1000 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 21565 | 64166 | 0.33608 | 17.3% | 20449 | 0.31869 | 20097 | 0.49 | 0.3 | -5.175% | 5.175% | quarter | 0.19 | 1.25
UAE - EAST VILLE Fujeirah - C | 2026-03 | UAE | C | 31 | 800 + 500 + 350 + 1000 | Cummins QSG12 (350 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 39443 | 119660 | 0.32963 | 14.1% | 35589 | 0.29742 | 35741 | 0.49 | 0.3 | -9.771% | 9.771% | quarter | 0.28 | 1.236
UAE - EAST VILLE Fujeirah - C | 2026-04 | UAE | C | 30 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 40908 | 134024 | 0.30523 | 31.5% | 41196 | 0.30738 | 40884 | 0.73 | 0.38 | 0.704% | 0.704% | quarter | 0.39 | 0.982
UAE - EAST VILLE Fujeirah - C | 2026-05 | UAE | C | 31 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 81962 | 292561 | 0.28015 | 32.9% | 85640 | 0.29273 | 83125 | 0.73 | 0.38 | 4.487% | 4.487% | quarter | 0.45 | 1.031
UAE - EAST VILLE Fujeirah - C | 2026-06 | UAE | C | 30 | 500 + 1000 + 800 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 93739 | 337635 | 0.27763 | 28.4% | 94693 | 0.28046 | 94523 | 0.73 | 0.38 | 1.018% | 1.018% | quarter | 0.47 | 0.966
UAE - EAST VILLE Fujeirah - C | 2026-07 | UAE | C | 31 | 800 + 1000 + 1250 + 500 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 113910 | 392398 | 0.29029 | 26.7% | 108780 | 0.27722 | 112234 | 0.73 | 0.45 | -4.504% | 4.504% | quarter | 0.45 | 1.01
UAE - EAST VILLE Fujeirah - C | 2026-08 | UAE | C | 31 | 1250 + 800 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 136070 | 469656 | 0.28972 | 21.6% | 136740 | 0.29115 | 134786 | 0.73 | 0.45 | 0.4924% | 0.4924% | quarter | 0.51 | 1.086
UAE - EAST VILLE Fujeirah - C | 2026-09 | UAE | C | 30 | 1250 + 800 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 127919 | 436297 | 0.29319 | 20.5% | 127028 | 0.29115 | 124483 | 0.73 | 0.45 | -0.6965% | 0.6965% | quarter | 0.52 | 1.214
UAE - EAST VILLE Hubshan - C | 2025-01 | UAE | C | 31 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 33076 | 103691 | 0.31899 | 0% | 32819 | 0.31651 | 33491 | 0.7 | 0.31 | -0.777% | 0.777% | quarter | 0.35 | 0.992
UAE - EAST VILLE Hubshan - C | 2025-02 | UAE | C | 28 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 35810 | 118945 | 0.30106 | 0% | 36450 | 0.30644 | 36624 | 0.7 | 0.31 | 1.787% | 1.787% | quarter | 0.42 | 1.036
UAE - EAST VILLE Hubshan - C | 2025-03 | UAE | C | 30 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 51168 | 188212 | 0.27186 | 0% | 56273 | 0.29899 | 56500 | 0.7 | 0.31 | 9.977% | 9.977% | quarter | 0.45 | 1.112
UAE - EAST VILLE Hubshan - C | 2025-07 | UAE | C | 31 | 800 + 1000 + 1250 + 500 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 187137 | 671080 | 0.27886 | 0% | 190818 | 0.28434 | 189465 | 0.73 | 0.49 | 1.967% | 1.967% | quarter | 0.49 | 1.25
UAE - EAST VILLE Hubshan - C | 2025-08 | UAE | C | 31 | 1250 + 800 + 1000 + 1000 + 500 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 249326 | 907081 | 0.27487 | 0% | 256727 | 0.28303 | 257925 | 0.73 | 0.49 | 2.968% | 2.968% | quarter | 0.59 | 1.25
UAE - EAST VILLE Hubshan - C | 2025-09 | UAE | C | 30 | 1250 + 1000 + 800 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 220047 | 800197 | 0.27499 | 0.6% | 226685 | 0.28329 | 227987 | 0.73 | 0.49 | 3.017% | 3.017% | quarter | 0.57 | 0.974
UAE - EAST VILLE Hubshan - C | 2025-11 | UAE | C | 30 | 1250 + 1000 + 800 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 89169 | 306001 | 0.2914 | 13% | 94360 | 0.30837 | 93939 | 0.67 | 0.38 | 5.822% | 5.822% | quarter | 0.39 | 0.954
UAE - EAST VILLE Hubshan - C | 2025-12 | UAE | C | 31 | 1000 + 800 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 66601 | 243441 | 0.27358 | 15.2% | 72135 | 0.29631 | 73009 | 0.67 | 0.38 | 8.309% | 8.309% | quarter | 0.39 | 1.009
UAE - EAST VILLE Hubshan - C | 2026-01 | UAE | C | 31 | 1000 + 800 + 1000 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 57262 | 209525 | 0.27329 | 18.4% | 63676 | 0.30391 | 64418 | 0.67 | 0.37 | 11.2% | 11.2% | quarter | 0.35 | 1.016
UAE - EAST VILLE Hubshan - C | 2026-02 | UAE | C | 28 | 1000 + 800 + 1250 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 67125 | 245343 | 0.2736 | 18.5% | 71749 | 0.29244 | 72059 | 0.67 | 0.37 | 6.889% | 6.889% | quarter | 0.4 | 0.996
UAE - EAST VILLE Hubshan - C | 2026-03 | UAE | C | 31 | 1250 + 800 + 1000 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 95687 | 344776 | 0.27753 | 14.3% | 103765 | 0.30096 | 100144 | 0.67 | 0.37 | 8.442% | 8.442% | quarter | 0.42 | 1.14
UAE - EAST VILLE Hubshan - C | 2026-04 | UAE | C | 30 | 1250 + 800 + 1000 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 103494 | 366049 | 0.28273 | 16% | 109843 | 0.30008 | 109543 | 0.68 | 0.41 | 6.135% | 6.135% | quarter | 0.43 | 0.953
UAE - EAST VILLE Hubshan - C | 2026-05 | UAE | C | 31 | 1250 + 800 + 1000 + 1250 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 173232 | 584637 | 0.29631 | 15.3% | 168689 | 0.28854 | 170109 | 0.68 | 0.41 | -2.622% | 2.622% | quarter | 0.51 | 0.963
UAE - EAST VILLE Hubshan - C | 2026-06 | UAE | C | 30 | 1250 + 1250 + 800 + 1000 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 175015 | 604118 | 0.2897 | 22.1% | 177345 | 0.29356 | 176136 | 0.68 | 0.41 | 1.331% | 1.331% | quarter | 0.51 | 0.973
UAE - EAST VILLE Hubshan - C | 2026-07 | UAE | C | 31 | 1250 + 1250 + 800 + 1000 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 224091 | 785180 | 0.2854 | 17.3% | 228551 | 0.29108 | 228292 | 0.68 | 0.46 | 1.99% | 1.99% | quarter | 0.53 | 0.991
UAE - EAST VILLE Hubshan - C | 2026-08 | UAE | C | 31 | 1250 + 800 + 1250 + 1000 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 281834 | 1005624 | 0.28026 | 13.7% | 288232 | 0.28662 | 284998 | 0.68 | 0.46 | 2.27% | 2.27% | quarter | 0.55 | 1.185
UAE - EAST VILLE Hubshan - C | 2026-09 | UAE | C | 30 | 1250 + 800 + 1000 + 1250 + 1000 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 248421 | 875972 | 0.28359 | 14.9% | 249252 | 0.28454 | 252170 | 0.68 | 0.46 | 0.3345% | 0.3345% | quarter | 0.55 | 1.034
UAE - ENATA - I | 2025-01 | UAE | I | 31 | 500 + 500 + 300 + 60 | JCB 448 (60 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 21372 | 46984 | 0.45488 | 22.4% | 18996 | 0.40431 | 20561 | 0.45 | 0.18 | -11.12% | 11.12% | site | 0.16 | 0.977
UAE - Galfar - C | 2025-03 | UAE | C | 26 | 800 + 800 + 800 | Cummins QSK23 (800 kVA) | 81117 | 288050 | 0.28161 | 0% | 79096 | 0.27459 | 77916 | 0.68 | 0.38 | -2.491% | 2.491% | quarter | 0.5 | 1.25
UAE - Galfar - C | 2025-04 | UAE | C | 30 | 800 + 800 + 800 | Cummins QSK23 (800 kVA) | 115428 | 416005 | 0.27747 | 4% | 113877 | 0.27374 | 113272 | 0.68 | 0.41 | -1.344% | 1.344% | quarter | 0.51 | 1.117
UAE - Galfar - C | 2025-05 | UAE | C | 31 | 800 + 800 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 124528 | 438001 | 0.28431 | 13.5% | 120116 | 0.27424 | 119568 | 0.68 | 0.41 | -3.543% | 3.543% | quarter | 0.51 | 1.043
UAE - Galfar - C | 2025-06 | UAE | C | 30 | 800 + 800 + 1000 + 800 + 1000 + 800 + 800 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 158643 | 527634 | 0.30067 | 16.2% | 144500 | 0.27386 | 145842 | 0.68 | 0.41 | -8.915% | 8.915% | quarter | 0.51 | 0.991
UAE - Galfar - C | 2025-08 | UAE | C | 31 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 198777 | 727670 | 0.27317 | 17.6% | 197240 | 0.27106 | 195982 | 0.7 | 0.45 | -0.7732% | 0.7732% | quarter | 0.56 | 1.185
UAE - Galfar - C | 2025-09 | UAE | C | 30 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 150281 | 548661 | 0.27391 | 21.2% | 148788 | 0.27118 | 149459 | 0.7 | 0.45 | -0.9935% | 0.9935% | quarter | 0.54 | 0.974
UAE - Galfar - C | 2025-10 | UAE | C | 31 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 127286 | 430104 | 0.29594 | 24.5% | 119169 | 0.27707 | 120427 | 0.66 | 0.35 | -6.377% | 6.377% | quarter | 0.46 | 0.986
UAE - Galfar - C | 2025-11 | UAE | C | 30 | 800 + 800 + 800 + 500 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 84323 | 278579 | 0.30269 | 26.4% | 78194 | 0.28069 | 80993 | 0.66 | 0.35 | -7.268% | 7.268% | quarter | 0.43 | 0.927
UAE - Galfar - C | 2025-12 | UAE | C | 31 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 69577 | 243531 | 0.2857 | 24.9% | 69681 | 0.28613 | 70738 | 0.66 | 0.35 | 0.1495% | 0.1495% | quarter | 0.4 | 1
UAE - Galfar - C | 2026-01 | UAE | C | 31 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 66151 | 220890 | 0.29947 | 25.8% | 64325 | 0.29121 | 64854 | 0.65 | 0.34 | -2.76% | 2.76% | quarter | 0.37 | 0.947
UAE - Galfar - C | 2026-02 | UAE | C | 28 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 69319 | 237652 | 0.29168 | 29.1% | 67694 | 0.28485 | 67882 | 0.65 | 0.34 | -2.344% | 2.344% | quarter | 0.4 | 0.943
UAE - Galfar - C | 2026-03 | UAE | C | 31 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 86720 | 294297 | 0.29467 | 32.3% | 82780 | 0.28128 | 83557 | 0.65 | 0.34 | -4.543% | 4.543% | quarter | 0.42 | 0.973
UAE - Galfar - C | 2026-04 | UAE | C | 30 | 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 93921 | 323281 | 0.29052 | 33.4% | 91745 | 0.28379 | 91744 | 0.59 | 0.34 | -2.317% | 2.317% | quarter | 0.39 | 0.953
UAE - Galfar - C | 2026-05 | UAE | C | 31 | 800 + 800 + 800 + 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Cummins QSX15 (500 kVA) | 132742 | 447940 | 0.29634 | 37.5% | 125284 | 0.27969 | 125633 | 0.59 | 0.34 | -5.618% | 5.618% | quarter | 0.42 | 0.988
UAE - Galfar - C | 2026-07 | UAE | C | 31 | 800 + 800 + 800 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 189084 | 631022 | 0.29965 | 31.5% | 174170 | 0.27601 | 175673 | 0.61 | 0.37 | -7.887% | 7.887% | quarter | 0.46 | 0.944
UAE - Galfar - C | 2026-08 | UAE | C | 31 | 800 + 800 + 800 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 219106 | 740168 | 0.29602 | 27.1% | 204734 | 0.2766 | 204510 | 0.61 | 0.37 | -6.559% | 6.559% | quarter | 0.46 | 0.958
UAE - Galfar - C | 2026-09 | UAE | C | 30 | 800 + 800 + 800 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA) | 181141 | 609159 | 0.29736 | 29.5% | 168279 | 0.27625 | 168099 | 0.61 | 0.37 | -7.101% | 7.101% | quarter | 0.46 | 0.957
UAE - Innovo Build - S | 2025-01 | UAE | S | 31 | 125 + 350 + 300 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 6891 | 14157 | 0.48676 | 23.4% | 6461 | 0.45638 | 6473 | 0.45 | 0.04 | -6.24% | 6.24% | quarter | 0.17 | 0.955
UAE - Innovo Build - S | 2025-03 | UAE | S | 31 | 125 + 350 + 125 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA) | 8521 | 17492 | 0.48714 | 27% | 7857 | 0.44918 | 7394 | 0.45 | 0.04 | -7.793% | 7.793% | quarter | 0.15 | 0.935
UAE - Innovo Build - S | 2025-05 | UAE | S | 31 | 125 + 250 + 350 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA) | 17276 | 46770 | 0.36938 | 26.3% | 16872 | 0.36074 | 15703 | 0.45 | 0.29 | -2.339% | 2.339% | quarter | 0.28 | 0.952
UAE - Innovo Build - S | 2025-06 | UAE | S | 29 | 125 + 250 + 350 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA) | 16849 | 47893 | 0.35181 | 23.4% | 16728 | 0.34928 | 15432 | 0.45 | 0.29 | -0.7181% | 0.7181% | quarter | 0.32 | 1.076
UAE - Innovo Build - S | 2025-07 | UAE | S | 31 | 350 + 125 + 250 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA) | 21645 | 65678 | 0.32956 | 20.1% | 20702 | 0.3152 | 20800 | 0.51 | 0.21 | -4.357% | 4.357% | quarter | 0.27 | 0.958
UAE - Innovo Build - S | 2025-08 | UAE | S | 31 | 350 + 125 + 250 + 350 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA) | 24801 | 71203 | 0.34831 | 18.7% | 22671 | 0.3184 | 22160 | 0.51 | 0.21 | -8.588% | 8.588% | quarter | 0.27 | 1.177
UAE - Innovo Build - S | 2025-09 | UAE | S | 30 | 350 + 350 + 125 + 125 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA) | 19937 | 58083 | 0.34325 | 20.1% | 18043 | 0.31064 | 18190 | 0.51 | 0.21 | -9.5% | 9.5% | quarter | 0.24 | 1.25
UAE - Innovo Build - S | 2025-10 | UAE | S | 31 | 350 + 125 + 350 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA) | 18047 | 45014 | 0.40092 | 21.9% | 14123 | 0.31375 | 14445 | 0.45 | 0.26 | -21.74% | 21.74% | quarter | 0.22 | 0.993
UAE - Innovo Build - S | 2025-11 | UAE | S | 30 | 125 + 350 + 125 + 125 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA) | 11164 | 26408 | 0.42275 | 24.3% | 9640 | 0.36504 | 8989 | 0.45 | 0.26 | -13.65% | 13.65% | quarter | 0.24 | 1.25
UAE - Innovo Build - S | 2025-12 | UAE | S | 31 | 125 + 125 + 350 + 125 + 300 | Cummins QSG12 (350 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 8560 | 17646 | 0.4851 | 13.4% | 7443 | 0.4218 | 7444 | 0.45 | 0.26 | -13.05% | 13.05% | quarter | 0.21 | 0.947
UAE - Innovo Build - S | 2026-01 | UAE | S | 31 | 125 + 125 + 125 + 300 | JCB 448 (125 kVA), JD 6090 (300 kVA) | 4962 | 9831 | 0.50473 | 27% | 5240 | 0.53301 | 5305 | 0.53 | 0.3 | 5.603% | 5.603% | quarter | 0.13 | 0.875
UAE - Innovo Build - S | 2026-02 | UAE | S | 28 | 125 + 125 + 125 | JCB 448 (125 kVA) | 5888 | 13076 | 0.45029 | 20.2% | 5248 | 0.40135 | 5326 | 0.53 | 0.3 | -10.87% | 10.87% | quarter | 0.25 | 1.141
UAE - Innovo Build - S | 2026-03 | UAE | S | 31 | 125 + 125 | JCB 448 (125 kVA) | 6374 | 14843 | 0.42943 | 17.7% | 6272 | 0.42256 | 6464 | 0.53 | 0.3 | -1.6% | 1.6% | quarter | 0.22 | 0.998
UAE - Innovo Build - S | 2026-04 | UAE | S | 30 | 125 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7995 | 19768 | 0.40444 | 26.9% | 8322 | 0.42098 | 8372 | 0.52 | 0.32 | 4.09% | 4.09% | quarter | 0.23 | 0.929
UAE - Innovo Build - S | 2026-05 | UAE | S | 30 | 125 + 220 + 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 12019 | 29714 | 0.40449 | 33% | 11643 | 0.39184 | 11539 | 0.52 | 0.32 | -3.128% | 3.128% | quarter | 0.32 | 1.22
UAE - Innovo Build - S | 2026-06 | UAE | S | 30 | 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 14532 | 36786 | 0.39504 | 27.9% | 14771 | 0.40154 | 14282 | 0.52 | 0.32 | 1.645% | 1.645% | quarter | 0.36 | 1.25
UAE - Intermass - S | 2025-01 | UAE | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 3913 | 8294 | 0.47179 | 7.1% | 4023 | 0.48505 | 3995 | 0.45 | 0.11 | 2.811% | 2.811% | site | 0.16 | 1.058
UAE - Intermass - S | 2025-02 | UAE | S | 28 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 4283 | 9295 | 0.46079 | 11.8% | 4224 | 0.45444 | 4523 | 0.45 | 0.11 | -1.378% | 1.378% | site | 0.17 | 1.072
UAE - Intermass - S | 2025-03 | UAE | S | 27 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 4573 | 8771 | 0.52138 | 15% | 3857 | 0.43974 | 3826 | 0.45 | 0.11 | -15.66% | 15.66% | site | 0.19 | 1.25
UAE - Intermass - S | 2025-04 | UAE | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 10399 | 23584 | 0.44093 | 22.1% | 8989 | 0.38115 | 10450 | 0.51 | 0.21 | -13.56% | 13.56% | quarter | 0.27 | 1.031
UAE - Intermass - S | 2025-05 | UAE | S | 31 | 125 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 12551 | 29556 | 0.42465 | 23% | 11772 | 0.39829 | 12090 | 0.51 | 0.21 | -6.207% | 6.207% | quarter | 0.28 | 0.993
UAE - Intermass - S | 2025-06 | UAE | S | 28 | 125 + 220 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 12398 | 29810 | 0.4159 | 19.6% | 11462 | 0.3845 | 11164 | 0.51 | 0.21 | -7.55% | 7.55% | quarter | 0.31 | 1.196
UAE - Intermass - S | 2025-07 | UAE | S | 31 | 125 + 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 16549 | 40882 | 0.4048 | 16.5% | 15318 | 0.37469 | 14664 | 0.58 | 0.33 | -7.439% | 7.439% | quarter | 0.36 | 1.25
UAE - Intermass - S | 2025-08 | UAE | S | 31 | 125 + 220 + 125 | JCB 448 (125 kVA), unlisted 200–220 kVA | 15694 | 37704 | 0.41624 | 19% | 14362 | 0.38091 | 14089 | 0.58 | 0.33 | -8.487% | 8.487% | quarter | 0.34 | 1.095
UAE - Intermass - S | 2025-09 | UAE | S | 30 | 125 + 220 + 125 + 125 | JCB 448 (125 kVA), unlisted 200–220 kVA | 12399 | 29155 | 0.42528 | 19.2% | 11305 | 0.38776 | 11629 | 0.58 | 0.33 | -8.823% | 8.823% | quarter | 0.31 | 0.969
UAE - Intermass - S | 2025-10 | UAE | S | 31 | 125 + 220 + 125 | JCB 448 (125 kVA), unlisted 200–220 kVA | 10359 | 23660 | 0.43783 | 21.5% | 9567 | 0.40435 | 9398 | 0.5 | 0.31 | -7.646% | 7.646% | quarter | 0.25 | 1.051
UAE - Intermass - S | 2025-11 | UAE | S | 30 | 125 + 125 + 125 + 220 | JCB 448 (125 kVA), unlisted 200–220 kVA | 6751 | 14272 | 0.47302 | 20.3% | 5872 | 0.41143 | 6220 | 0.5 | 0.31 | -13.02% | 13.02% | quarter | 0.22 | 1.031
UAE - Intermass - S | 2025-12 | UAE | S | 31 | 125 + 125 + 125 + 220 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA), unlisted 200–220 kVA | 4558 | 8227 | 0.55403 | 23.6% | 4031 | 0.48997 | 4151 | 0.5 | 0.31 | -11.56% | 11.56% | quarter | 0.15 | 1.033
UAE - Intermass - S | 2026-01 | UAE | S | 31 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 4216 | 5784 | 0.72891 | 37.6% | 3332 | 0.57607 | 3421 | 0.45 | 0.05 | -20.97% | 20.97% | quarter | 0.11 | 0.905
UAE - Intermass - S | 2026-04 | UAE | S | 30 | 125 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 5451 | 11278 | 0.48333 | 26% | 5074 | 0.4499 | 5612 | 0.45 | 0.13 | -6.916% | 6.916% | quarter | 0.18 | 0.996
UAE - Intermass - S | 2026-05 | UAE | S | 31 | 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 5978 | 11726 | 0.50981 | 33.2% | 7266 | 0.61965 | 6227 | 0.45 | 0.13 | 21.55% | 21.55% | quarter | 0.14 | 1.124
UAE - Intermass - S | 2026-06 | UAE | S | 30 | 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 6102 | 14000 | 0.43586 | 32.7% | 7842 | 0.56014 | 7189 | 0.45 | 0.13 | 28.52% | 28.52% | quarter | 0.17 | 1.1
UAE - Intermass - S | 2026-07 | UAE | S | 31 | 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 7486 | 15704 | 0.47669 | 35% | 8338 | 0.53095 | 8015 | 0.45 | 0.1 | 11.38% | 11.38% | quarter | 0.19 | 1.109
UAE - Intermass - S | 2026-08 | UAE | S | 31 | 220 + 125 + 125 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 6268 | 12351 | 0.50749 | 31% | 7677 | 0.62157 | 6548 | 0.45 | 0.1 | 22.48% | 22.48% | quarter | 0.14 | 1.105
UAE - KITOPI Alqouz- I | 2025-01 | UAE | I | 23 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 11691 | 31556 | 0.37048 | 10.5% | 12680 | 0.40183 | 12734 | 0.45 | 0.15 | 8.459% | 8.459% | quarter | 0.21 | 1.028
UAE - KITOPI Alqouz- I | 2025-02 | UAE | I | 25 | 300 + 220 + 220 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 13933 | 32755 | 0.42537 | 13% | 14960 | 0.45672 | 14139 | 0.45 | 0.15 | 7.371% | 7.371% | quarter | 0.26 | 1.25
UAE - KITOPI Alqouz- I | 2025-04 | UAE | I | 29 | 220 + 300 | JD 6068 (220 kVA), JD 6090 (300 kVA) | 18615 | 44721 | 0.41625 | 20% | 20131 | 0.45015 | 17842 | 0.45 | 0.16 | 8.144% | 8.144% | site | 0.28 | 1.118
UAE - KITOPI Alqouz- I | 2025-05 | UAE | I | 31 | 250 + 300 + 220 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA), JD 6090 (300 kVA) | 18678 | 53039 | 0.35216 | 19.8% | 21214 | 0.39997 | 18708 | 0.45 | 0.16 | 13.58% | 13.58% | site | 0.28 | 1.058
UAE - KITOPI Alqouz- I | 2025-06 | UAE | I | 30 | 300 | JD 6090 (300 kVA) | 19057 | 58595 | 0.32523 | 15.2% | 25093 | 0.42824 | 24248 | 0.45 | 0.16 | 31.67% | 31.67% | site | 0.34 | 1.25
UAE - KITOPI Alqouz- I | 2025-07 | UAE | I | 31 | 300 | JD 6090 (300 kVA) | 20942 | 62054 | 0.33748 | 16.6% | 26012 | 0.41918 | 25149 | 0.45 | 0.16 | 24.21% | 24.21% | site | 0.38 | 1.25
UAE - KITOPI Alqouz- I | 2025-08 | UAE | I | 31 | 300 | JD 6090 (300 kVA) | 20405 | 56986 | 0.35807 | 15.2% | 24430 | 0.4287 | 23575 | 0.45 | 0.16 | 19.73% | 19.73% | site | 0.34 | 1.25
UAE - KITOPI Alqouz- I | 2025-09 | UAE | I | 30 | 300 + 250 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 19160 | 56614 | 0.33843 | 14.3% | 24206 | 0.42756 | 20767 | 0.45 | 0.16 | 26.34% | 26.34% | site | 0.28 | 1.25
UAE - KITOPI Alqouz- I | 2025-10 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 18697 | 54046 | 0.34595 | 13.1% | 20976 | 0.38811 | 18568 | 0.45 | 0.16 | 12.19% | 12.19% | quarter | 0.3 | 1.028
UAE - KITOPI Alqouz- I | 2025-11 | UAE | I | 30 | 220 + 300 + 250 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA), unlisted 200–220 kVA | 17560 | 40749 | 0.43093 | 13.3% | 17589 | 0.43164 | 17399 | 0.45 | 0.16 | 0.1651% | 0.1651% | quarter | 0.31 | 1.021
UAE - KITOPI Alqouz- I | 2025-12 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 12620 | 32727 | 0.38561 | 13% | 13025 | 0.39799 | 13052 | 0.45 | 0.16 | 3.209% | 3.209% | quarter | 0.22 | 0.993
UAE - KITOPI Alqouz- I | 2026-01 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 12484 | 31018 | 0.40248 | 15.8% | 12639 | 0.40747 | 12706 | 0.45 | 0.16 | 1.242% | 1.242% | site | 0.21 | 0.999
UAE - KITOPI Alqouz- I | 2026-02 | UAE | I | 28 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 12053 | 31073 | 0.38789 | 15.2% | 12138 | 0.39063 | 12202 | 0.45 | 0.16 | 0.7052% | 0.7052% | site | 0.23 | 0.984
UAE - KITOPI Alqouz- I | 2026-03 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 13236 | 33907 | 0.39036 | 13.6% | 13107 | 0.38656 | 13299 | 0.45 | 0.16 | -0.9746% | 0.9746% | site | 0.24 | 1.054
UAE - KITOPI Alqouz- I | 2026-04 | UAE | I | 30 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 12614 | 33696 | 0.37435 | 17.2% | 13089 | 0.38844 | 13137 | 0.45 | 0.16 | 3.766% | 3.766% | site | 0.23 | 0.994
UAE - KITOPI Alqouz- I | 2026-05 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 14895 | 45962 | 0.32407 | 19.4% | 16628 | 0.36178 | 16392 | 0.45 | 0.16 | 11.63% | 11.63% | site | 0.3 | 1.042
UAE - KITOPI Alqouz- I | 2026-06 | UAE | I | 30 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 14272 | 45528 | 0.31348 | 19.5% | 16360 | 0.35934 | 16147 | 0.45 | 0.16 | 14.63% | 14.63% | site | 0.31 | 0.953
UAE - KITOPI Alqouz- I | 2026-07 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 17330 | 54549 | 0.3177 | 17.1% | 20394 | 0.37387 | 18641 | 0.45 | 0.16 | 17.68% | 17.68% | site | 0.31 | 0.989
UAE - KITOPI Alqouz- I | 2026-08 | UAE | I | 31 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 17310 | 54495 | 0.31764 | 16.2% | 20275 | 0.37205 | 18484 | 0.45 | 0.16 | 17.13% | 17.13% | site | 0.32 | 0.995
UAE - KITOPI Alqouz- I | 2026-09 | UAE | I | 30 | 250 + 300 | Cummins QSL9 (250–300 kVA), JD 6090 (300 kVA) | 18532 | 56164 | 0.32996 | 14.3% | 23245 | 0.41388 | 18973 | 0.45 | 0.16 | 25.43% | 25.43% | site | 0.26 | 1.022
UAE - MNH Fujairah - C | 2026-07 | UAE | C | 31 | 350 + 500 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA) | 58859 | 200875 | 0.29301 | 6.6% | 62382 | 0.31055 | 61616 | 0.68 | 0.42 | 5.985% | 5.985% | quarter | 0.43 | 1.022
UAE - MNH Fujairah - C | 2026-08 | UAE | C | 31 | 500 + 350 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA) | 52062 | 173224 | 0.30055 | 22.2% | 52835 | 0.30501 | 53020 | 0.68 | 0.42 | 1.485% | 1.485% | quarter | 0.48 | 1.011
UAE - MNH Fujairah - C | 2026-09 | UAE | C | 30 | 500 + 350 + 500 | Cummins QSG12 (350 kVA), Volvo TAD1651 (500 kVA) | 86620 | 294314 | 0.29431 | 12.7% | 89377 | 0.30368 | 89117 | 0.68 | 0.42 | 3.183% | 3.183% | quarter | 0.51 | 1.008
UAE - Natural Fragrances - I | 2025-04 | UAE | I | 29 | 250 | Cummins QSL9 (250–300 kVA) | 5596 | 17762 | 0.31505 | 16.2% | 6109 | 0.34394 | 6071 | 0.5 | 0.3 | 9.167% | 9.167% | default | 0.31 | 1.096
UAE - Natural Fragrances - I | 2025-05 | UAE | I | 30 | 250 | Cummins QSL9 (250–300 kVA) | 7714 | 24825 | 0.31074 | 15.6% | 7985 | 0.32165 | 7966 | 0.5 | 0.3 | 3.513% | 3.513% | default | 0.4 | 1.113
UAE - Natural Fragrances - I | 2025-06 | UAE | I | 26 | 250 | Cummins QSL9 (250–300 kVA) | 6365 | 19830 | 0.32098 | 15.9% | 6378 | 0.32163 | 6378 | 0.5 | 0.3 | 0.2042% | 0.2042% | default | 0.4 | 1.069
UAE - Natural Fragrances - I | 2025-07 | UAE | I | 30 | 250 | Cummins QSL9 (250–300 kVA) | 8918 | 28214 | 0.31608 | 11.8% | 8749 | 0.31009 | 8741 | 0.5 | 0.3 | -1.895% | 1.895% | default | 0.48 | 1.073
UAE - Natural Fragrances - I | 2025-09 | UAE | I | 30 | 250 | Cummins QSL9 (250–300 kVA) | 8705 | 27064 | 0.32164 | 11.3% | 8539 | 0.31551 | 8537 | 0.5 | 0.3 | -1.907% | 1.907% | default | 0.43 | 1.038
UAE - Natural Fragrances - I | 2025-10 | UAE | I | 31 | 250 | Cummins QSL9 (250–300 kVA) | 8013 | 21975 | 0.36464 | 11% | 7231 | 0.32906 | 7228 | 0.5 | 0.3 | -9.759% | 9.759% | default | 0.36 | 1.067
UAE - Natural Fragrances - I | 2025-12 | UAE | I | 30 | 250 | Cummins QSL9 (250–300 kVA) | 5524 | 12607 | 0.43817 | 6.9% | 5135 | 0.40731 | 5143 | 0.5 | 0.3 | -7.042% | 7.042% | default | 0.2 | 1
UAE - Natural Fragrances - I | 2026-01 | UAE | I | 30 | 250 | Cummins QSL9 (250–300 kVA) | 4810 | 10122 | 0.4752 | 5.9% | 4697 | 0.46404 | 4709 | 0.5 | 0.3 | -2.349% | 2.349% | default | 0.15 | 1.048
UAE - Nordic - I | 2025-01 | UAE | I | 31 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA) | 26608 | 80742 | 0.32954 | 10.7% | 29895 | 0.37025 | 28520 | 0.65 | 0.36 | 12.35% | 12.35% | site | 0.29 | 1.092
UAE - Nordic - I | 2025-02 | UAE | I | 28 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA) | 24915 | 77728 | 0.32054 | 9.7% | 25302 | 0.32552 | 25020 | 0.65 | 0.36 | 1.553% | 1.553% | site | 0.35 | 1.223
UAE - Nordic - I | 2025-03 | UAE | I | 31 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA) | 21997 | 58585 | 0.37547 | 16% | 24758 | 0.4226 | 22273 | 0.65 | 0.36 | 12.55% | 12.55% | site | 0.24 | 1.25
UAE - Nordic - I | 2025-04 | UAE | I | 30 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA) | 27037 | 82249 | 0.32872 | 16% | 30344 | 0.36893 | 29681 | 0.65 | 0.35 | 12.23% | 12.23% | quarter | 0.29 | 1.051
UAE - Nordic - I | 2025-05 | UAE | I | 31 | 500 + 300 + 350 + 300 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA), JD 6090 (300 kVA) | 38579 | 124282 | 0.31042 | 14.2% | 37584 | 0.30241 | 38168 | 0.65 | 0.35 | -2.579% | 2.579% | quarter | 0.41 | 1.023
UAE - Nordic - I | 2025-07 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 42034 | 136598 | 0.30772 | 12.5% | 39050 | 0.28588 | 40323 | 0.65 | 0.36 | -7.099% | 7.099% | quarter | 0.45 | 1.014
UAE - Nordic - I | 2025-08 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 44765 | 144761 | 0.30923 | 11.2% | 40794 | 0.2818 | 41351 | 0.65 | 0.36 | -8.871% | 8.871% | quarter | 0.48 | 1.14
UAE - Nordic - I | 2025-09 | UAE | I | 30 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 29365 | 90765 | 0.32353 | 13.6% | 29052 | 0.32008 | 28160 | 0.65 | 0.36 | -1.066% | 1.066% | quarter | 0.36 | 1.25
UAE - Nordic - I | 2025-10 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 43159 | 143082 | 0.30164 | 9.7% | 39555 | 0.27645 | 40704 | 0.64 | 0.36 | -8.351% | 8.351% | quarter | 0.49 | 1.039
UAE - Nordic - I | 2025-11 | UAE | I | 30 | 500 + 500 + 300 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 46006 | 146856 | 0.31327 | 7.3% | 44642 | 0.30398 | 45749 | 0.64 | 0.36 | -2.965% | 2.965% | quarter | 0.46 | 1
UAE - Nordic - I | 2025-12 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 44523 | 143212 | 0.31089 | 6.1% | 41346 | 0.2887 | 44303 | 0.64 | 0.36 | -7.136% | 7.136% | quarter | 0.45 | 1.012
UAE - Nordic - I | 2026-01 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 38446 | 121324 | 0.31689 | 8.3% | 37539 | 0.30941 | 39393 | 0.68 | 0.36 | -2.359% | 2.359% | quarter | 0.41 | 1.016
UAE - Nordic - I | 2026-02 | UAE | I | 28 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 38877 | 126184 | 0.3081 | 9.2% | 38135 | 0.30222 | 39764 | 0.68 | 0.36 | -1.909% | 1.909% | quarter | 0.46 | 0.982
UAE - Nordic - I | 2026-04 | UAE | I | 30 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 48304 | 151317 | 0.31922 | 10.2% | 44953 | 0.29708 | 47385 | 0.66 | 0.35 | -6.937% | 6.937% | quarter | 0.43 | 1.023
UAE - Nordic - I | 2026-05 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 45036 | 142243 | 0.31661 | 12.2% | 43988 | 0.30925 | 42824 | 0.66 | 0.35 | -2.327% | 2.327% | quarter | 0.4 | 1.053
UAE - Nordic - I | 2026-06 | UAE | I | 30 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 36774 | 114687 | 0.32065 | 13.2% | 36279 | 0.31633 | 36940 | 0.66 | 0.35 | -1.346% | 1.346% | quarter | 0.38 | 0.968
UAE - Nordic - I | 2026-07 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 43637 | 132877 | 0.3284 | 10.7% | 40902 | 0.30782 | 42993 | 0.62 | 0.32 | -6.268% | 6.268% | quarter | 0.4 | 1.007
UAE - Nordic - I | 2026-08 | UAE | I | 31 | 500 + 500 + 300 | Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 55704 | 168515 | 0.33056 | 8.9% | 52149 | 0.30946 | 54742 | 0.62 | 0.32 | -6.382% | 6.382% | quarter | 0.39 | 1.011
UAE - Nordic - I | 2026-09 | UAE | I | 30 | 500 + 500 + 500 + 300 | Cummins QSL9 (250–300 kVA), Cummins QSX15 (500 kVA), Volvo TAD1651 (500 kVA) | 66239 | 204195 | 0.32439 | 7.8% | 60092 | 0.29429 | 63630 | 0.62 | 0.32 | -9.28% | 9.28% | quarter | 0.44 | 1.053
UAE - SJ ABED - C | 2025-09 | UAE | C | 30 | 500 + 800 + 800 + 500 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 16816 | 45057 | 0.37322 | 30.6% | 18962 | 0.42084 | 18985 | 0.45 | 0.22 | 12.76% | 12.76% | quarter | 0.16 | 0.99
UAE - SJ ABED - C | 2025-10 | UAE | C | 31 | 500 + 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 21019 | 48823 | 0.43051 | 27.7% | 20070 | 0.41108 | 20080 | 0.47 | 0.24 | -4.515% | 4.515% | site | 0.17 | 1.04
UAE - SJ ABED - C | 2025-11 | UAE | C | 30 | 500 + 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 15358 | 34708 | 0.44249 | 23.4% | 17277 | 0.49778 | 18033 | 0.47 | 0.24 | 12.5% | 12.5% | site | 0.12 | 0.911
UAE - SJ ABED - C | 2025-12 | UAE | C | 31 | 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 21192 | 54257 | 0.39059 | 24.3% | 21532 | 0.39685 | 21582 | 0.47 | 0.24 | 1.604% | 1.604% | site | 0.18 | 0.994
UAE - SJ ABED - C | 2026-01 | UAE | C | 31 | 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 21430 | 58793 | 0.3645 | 24.9% | 22471 | 0.38221 | 22581 | 0.47 | 0.24 | 4.858% | 4.858% | site | 0.2 | 1
UAE - SJ ABED - C | 2026-02 | UAE | C | 28 | 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 20911 | 59288 | 0.3527 | 30.4% | 21691 | 0.36586 | 21761 | 0.47 | 0.24 | 3.73% | 3.73% | site | 0.22 | 0.995
UAE - SJ ABED - C | 2026-03 | UAE | C | 31 | 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 31303 | 75289 | 0.41577 | 31.6% | 25939 | 0.34453 | 25958 | 0.47 | 0.24 | -17.14% | 17.14% | site | 0.26 | 1.075
UAE - SJ ABED - C | 2026-04 | UAE | C | 30 | 500 + 800 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 28742 | 86280 | 0.33312 | 35% | 28935 | 0.33536 | 28621 | 0.56 | 0.29 | 0.6715% | 0.6715% | quarter | 0.28 | 0.99
UAE - SJ ABED - C | 2026-05 | UAE | C | 31 | 500 + 800 + 500 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 40382 | 131497 | 0.30709 | 32.6% | 41176 | 0.31313 | 39881 | 0.56 | 0.29 | 1.966% | 1.966% | quarter | 0.36 | 1.037
UAE - SJ ABED - C | 2026-06 | UAE | C | 30 | 800 + 500 + 500 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 42042 | 139943 | 0.30042 | 31.3% | 42954 | 0.30694 | 42393 | 0.56 | 0.29 | 2.169% | 2.169% | quarter | 0.3 | 0.97
UAE - SJ ABED - C | 2026-07 | UAE | C | 31 | 500 + 500 + 800 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 53657 | 175805 | 0.30521 | 28.8% | 56904 | 0.32368 | 52809 | 0.45 | 0.26 | 6.051% | 6.051% | quarter | 0.32 | 1.057
UAE - SJ ABED - C | 2026-08 | UAE | C | 31 | 500 + 800 + 500 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 54644 | 182481 | 0.29945 | 28.1% | 59468 | 0.32589 | 54102 | 0.45 | 0.26 | 8.828% | 8.828% | quarter | 0.29 | 1.099
UAE - SJ ABED - C | 2026-09 | UAE | C | 30 | 800 + 500 + 500 | Cummins QSK23 (800 kVA), Volvo TAD1651 (500 kVA) | 45524 | 147570 | 0.30849 | 29.2% | 46118 | 0.31252 | 46260 | 0.45 | 0.26 | 1.305% | 1.305% | quarter | 0.28 | 1.008
UAE - Seven Brothers - C | 2026-01 | UAE | C | 31 | 125 + 220 + 125 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 8079 | 16464 | 0.49071 | 12.7% | 6537 | 0.39705 | 7320 | 0.61 | 0.31 | -19.09% | 19.09% | quarter | 0.26 | 1.195
UAE - Seven Brothers - C | 2026-02 | UAE | C | 28 | 125 + 220 + 220 + 220 | JCB 448 (125 kVA), JD 6068 (220 kVA) | 12784 | 30695 | 0.41648 | 20.5% | 11769 | 0.38342 | 13397 | 0.61 | 0.31 | -7.94% | 7.94% | quarter | 0.33 | 0.985
UAE - Seven Brothers - C | 2026-03 | UAE | C | 31 | 220 + 220 + 125 + 250 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6068 (220 kVA) | 13885 | 30788 | 0.45099 | 17.8% | 13749 | 0.44657 | 13593 | 0.61 | 0.31 | -0.9795% | 0.9795% | quarter | 0.26 | 1.25
UAE - Seven Brothers - C | 2026-04 | UAE | C | 30 | 250 + 220 + 220 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA) | 15697 | 37775 | 0.41554 | 22.7% | 13764 | 0.36437 | 14819 | 0.63 | 0.31 | -12.31% | 12.31% | quarter | 0.27 | 0.989
UAE - Seven Brothers - C | 2026-05 | UAE | C | 31 | 250 + 220 + 220 | Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA) | 16469 | 46379 | 0.3551 | 24.1% | 16558 | 0.35702 | 16763 | 0.63 | 0.31 | 0.5404% | 0.5404% | quarter | 0.29 | 1.04
UAE - Seven Brothers - C | 2026-06 | UAE | C | 30 | 250 + 220 + 350 + 220 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), JD 6068 (220 kVA) | 20599 | 55930 | 0.3683 | 25.8% | 18607 | 0.33268 | 20961 | 0.63 | 0.31 | -9.67% | 9.67% | quarter | 0.37 | 0.967
UAE - Seven Brothers - C | 2026-07 | UAE | C | 31 | 350 + 220 + 220 | Cummins QSG12 (350 kVA), JD 6068 (220 kVA) | 23154 | 72648 | 0.31871 | 21.1% | 23769 | 0.32718 | 23883 | 0.72 | 0.43 | 2.656% | 2.656% | quarter | 0.35 | 0.98
UAE - Seven Brothers - C | 2026-09 | UAE | C | 30 | 500 + 350 + 500 + 250 | Cummins QSG12 (350 kVA), Cummins QSL9 (250–300 kVA), Volvo TAD1651 (500 kVA) | 68695 | 245832 | 0.27944 | 6.8% | 72657 | 0.29556 | 73531 | 0.72 | 0.43 | 5.768% | 5.768% | quarter | 0.58 | 1.014
UAE - Specialist - C | 2025-06 | UAE | C | 30 | 350 + 500 + 500 + 300 | Cummins QSG12 (350 kVA), Cummins QSX15 (500 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 37207 | 96115 | 0.38711 | 0% | 31754 | 0.33038 | 30967 | 0.45 | 0.27 | -14.66% | 14.66% | quarter | 0.29 | 1.071
UAE - Specialist - C | 2025-07 | UAE | C | 30 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 46558 | 118168 | 0.394 | 0% | 37329 | 0.3159 | 37695 | 0.63 | 0.25 | -19.82% | 19.82% | quarter | 0.35 | 1.25
UAE - Specialist - C | 2025-08 | UAE | C | 31 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 44292 | 130141 | 0.34034 | 5.2% | 40693 | 0.31268 | 40526 | 0.63 | 0.25 | -8.126% | 8.126% | quarter | 0.4 | 1.066
UAE - Specialist - C | 2025-09 | UAE | C | 30 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 28703 | 93122 | 0.30823 | 16.1% | 29234 | 0.31393 | 28500 | 0.63 | 0.25 | 1.85% | 1.85% | quarter | 0.39 | 1.25
UAE - Specialist - C | 2025-10 | UAE | C | 31 | 300 + 500 | JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 29956 | 81091 | 0.36941 | 16.5% | 34404 | 0.42426 | 32453 | 0.56 | 0.31 | 14.85% | 14.85% | site | 0.3 | 1.25
UAE - Specialist - C | 2025-11 | UAE | C | 30 | 350 + 300 + 500 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 27447 | 62770 | 0.43726 | 15.3% | 19921 | 0.31736 | 21200 | 0.56 | 0.31 | -27.42% | 27.42% | site | 0.36 | 1.25
UAE - Specialist - C | 2025-12 | UAE | C | 31 | 500 + 350 + 300 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 23228 | 57079 | 0.40694 | 15.2% | 20715 | 0.36292 | 20103 | 0.56 | 0.31 | -10.82% | 10.82% | site | 0.21 | 1.11
UAE - Specialist - C | 2026-01 | UAE | C | 31 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 18635 | 58308 | 0.3196 | 16.1% | 18940 | 0.32483 | 19068 | 0.56 | 0.31 | 1.637% | 1.637% | site | 0.3 | 1.098
UAE - Specialist - C | 2026-02 | UAE | C | 28 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 17761 | 55933 | 0.31754 | 18.1% | 17639 | 0.31536 | 17623 | 0.56 | 0.31 | -0.6869% | 0.6869% | site | 0.34 | 1.123
UAE - Specialist - C | 2026-03 | UAE | C | 31 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 20423 | 67629 | 0.30199 | 16.8% | 21218 | 0.31374 | 21080 | 0.56 | 0.31 | 3.893% | 3.893% | site | 0.36 | 1.25
UAE - Specialist - C | 2026-04 | UAE | C | 30 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 16889 | 54779 | 0.30831 | 21.5% | 17714 | 0.32337 | 17697 | 0.56 | 0.31 | 4.885% | 4.885% | quarter | 0.3 | 1.187
UAE - Specialist - C | 2026-05 | UAE | C | 31 | 350 + 500 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 21997 | 73583 | 0.29894 | 24.2% | 23488 | 0.3192 | 22614 | 0.56 | 0.31 | 6.778% | 6.778% | quarter | 0.33 | 1.25
UAE - Specialist - C | 2026-06 | UAE | C | 30 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 25113 | 77478 | 0.32413 | 21.2% | 26038 | 0.33607 | 25574 | 0.56 | 0.31 | 3.683% | 3.683% | quarter | 0.27 | 0.957
UAE - Specialist - C | 2026-07 | UAE | C | 31 | 500 + 300 + 350 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 35197 | 106862 | 0.32937 | 16.4% | 35415 | 0.33141 | 34262 | 0.45 | 0.31 | 0.6194% | 0.6194% | quarter | 0.32 | 0.942
UAE - Specialist - C | 2026-08 | UAE | C | 31 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 42020 | 129610 | 0.3242 | 12% | 40992 | 0.31627 | 40939 | 0.45 | 0.31 | -2.446% | 2.446% | quarter | 0.34 | 0.993
UAE - Specialist - C | 2026-09 | UAE | C | 30 | 500 + 350 + 300 | Cummins QSG12 (350 kVA), JD 6090 (300 kVA), Volvo TAD1651 (500 kVA) | 39012 | 118133 | 0.33024 | 12.8% | 37327 | 0.31597 | 37628 | 0.45 | 0.31 | -4.319% | 4.319% | quarter | 0.34 | 0.953
UAE - Target - C | 2025-04 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 219462 | 763281 | 0.28752 | 0% | 226914 | 0.29729 | 225442 | 0.75 | 0.37 | 3.396% | 3.396% | quarter | 0.53 | 1.113
UAE - Target - C | 2025-05 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 259823 | 939444 | 0.27657 | 0% | 278633 | 0.29659 | 275892 | 0.75 | 0.37 | 7.24% | 7.24% | quarter | 0.54 | 1.077
UAE - Target - C | 2025-06 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 281594 | 1002620 | 0.28086 | 0% | 296523 | 0.29575 | 296543 | 0.75 | 0.37 | 5.302% | 5.302% | quarter | 0.55 | 1.018
UAE - Target - C | 2025-07 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 320538 | 1139077 | 0.2814 | 3.9% | 337397 | 0.2962 | 335332 | 0.65 | 0.46 | 5.26% | 5.26% | quarter | 0.53 | 1.028
UAE - Target - C | 2025-08 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 339042 | 1201002 | 0.2823 | 10.4% | 354995 | 0.29558 | 354784 | 0.65 | 0.46 | 4.705% | 4.705% | quarter | 0.54 | 1.064
UAE - Target - C | 2025-09 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 245987 | 870613 | 0.28254 | 16.8% | 258395 | 0.2968 | 258281 | 0.65 | 0.46 | 5.044% | 5.044% | quarter | 0.52 | 0.956
UAE - Target - C | 2025-10 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 170159 | 597495 | 0.28479 | 24.7% | 178906 | 0.29943 | 179748 | 0.74 | 0.36 | 5.14% | 5.14% | quarter | 0.5 | 1.064
UAE - Target - C | 2025-11 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 98414 | 322694 | 0.30498 | 30% | 100958 | 0.31286 | 101465 | 0.74 | 0.36 | 2.585% | 2.585% | quarter | 0.41 | 0.995
UAE - Target - C | 2025-12 | UAE | C | 31 | 1250 + 1250 + 1250 + 800 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 68092 | 234902 | 0.28987 | 30.4% | 77476 | 0.32982 | 77113 | 0.74 | 0.36 | 13.78% | 13.78% | quarter | 0.34 | 1.06
UAE - Target - C | 2026-01 | UAE | C | 31 | 800 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 58834 | 203415 | 0.28923 | 25.4% | 60150 | 0.2957 | 62491 | 0.79 | 0.29 | 2.237% | 2.237% | quarter | 0.41 | 1.048
UAE - Target - C | 2026-02 | UAE | C | 28 | 800 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 66662 | 233080 | 0.286 | 32.6% | 68974 | 0.29592 | 70117 | 0.79 | 0.29 | 3.468% | 3.468% | quarter | 0.43 | 0.997
UAE - Target - C | 2026-03 | UAE | C | 31 | 800 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 95358 | 321081 | 0.29699 | 29.8% | 95218 | 0.29655 | 94272 | 0.79 | 0.29 | -0.1468% | 0.1468% | quarter | 0.44 | 1.25
UAE - Target - C | 2026-04 | UAE | C | 30 | 800 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 90140 | 315021 | 0.28614 | 35.1% | 94523 | 0.30005 | 91237 | 0.68 | 0.34 | 4.862% | 4.862% | quarter | 0.41 | 1.236
UAE - Target - C | 2026-05 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 + 800 | Cummins KTA50 (1250 kVA), Cummins QSK23 (800 kVA) | 157463 | 554499 | 0.28397 | 36.6% | 169518 | 0.30571 | 168235 | 0.68 | 0.34 | 7.656% | 7.656% | quarter | 0.43 | 1.021
UAE - Target - C | 2026-06 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 186309 | 642426 | 0.29001 | 33.6% | 194573 | 0.30287 | 196529 | 0.68 | 0.34 | 4.436% | 4.436% | quarter | 0.46 | 0.998
UAE - Target - C | 2026-07 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 242610 | 828580 | 0.2928 | 27.5% | 247909 | 0.2992 | 248232 | 0.7 | 0.38 | 2.184% | 2.184% | quarter | 0.5 | 1.034
UAE - Target - C | 2026-08 | UAE | C | 31 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 289932 | 991623 | 0.29238 | 21.9% | 295739 | 0.29824 | 294986 | 0.7 | 0.38 | 2.003% | 2.003% | quarter | 0.51 | 0.984
UAE - Target - C | 2026-09 | UAE | C | 30 | 1250 + 1250 + 1250 + 1250 | Cummins KTA50 (1250 kVA) | 248852 | 832563 | 0.2989 | 24.9% | 248273 | 0.2982 | 249769 | 0.7 | 0.38 | -0.2327% | 0.2327% | quarter | 0.51 | 1.006
UAE - Techshore - I | 2025-02 | UAE | I | 22 | 125 | JCB 448 (125 kVA) | 1744 | 2810 | 0.62064 | 13.5% | 1965 | 0.69929 | 1962 | 0.5 | 0.3 | 12.67% | 12.67% | default | 0.1 | 1.012
UAE - Techshore - I | 2025-03 | UAE | I | 25 | 125 | JCB 448 (125 kVA) | 1621 | 2824 | 0.57401 | 16% | 1821 | 0.64483 | 1825 | 0.5 | 0.3 | 12.34% | 12.34% | default | 0.12 | 0.99
UAE - Techshore - I | 2025-04 | UAE | I | 29 | 125 | JCB 448 (125 kVA) | 1963 | 3497 | 0.56134 | 21.7% | 2157 | 0.61681 | 2162 | 0.5 | 0.3 | 9.883% | 9.883% | default | 0.12 | 1.057
UAE - Techshore - I | 2025-05 | UAE | I | 31 | 125 | JCB 448 (125 kVA) | 2170 | 4155 | 0.52226 | 15.1% | 2339 | 0.56294 | 2349 | 0.5 | 0.3 | 7.788% | 7.788% | default | 0.14 | 1.014
UAE - Techshore - I | 2025-06 | UAE | I | 22 | 125 | JCB 448 (125 kVA) | 1922 | 4331 | 0.44378 | 7% | 2013 | 0.46479 | 2006 | 0.5 | 0.3 | 4.735% | 4.735% | default | 0.19 | 1.012
UAE - Techshore - I | 2025-07 | UAE | I | 27 | 125 | JCB 448 (125 kVA) | 2214 | 4774 | 0.46376 | 11.6% | 2320 | 0.48597 | 2320 | 0.5 | 0.3 | 4.788% | 4.788% | default | 0.18 | 1.091
UAE - Techshore - I | 2025-08 | UAE | I | 31 | 125 | JCB 448 (125 kVA) | 2849 | 6287 | 0.45316 | 4.2% | 2811 | 0.44711 | 2811 | 0.5 | 0.3 | -1.334% | 1.334% | default | 0.21 | 1.123
UAE - Techshore - I | 2025-09 | UAE | I | 30 | 125 | JCB 448 (125 kVA) | 2634 | 5271 | 0.49972 | 9.1% | 3018 | 0.57257 | 3013 | 0.5 | 0.3 | 14.58% | 14.58% | default | 0.14 | 0.99
UAE - Techshore - I | 2025-10 | UAE | I | 28 | 125 | JCB 448 (125 kVA) | 2089 | 4189 | 0.49869 | 7.5% | 2187 | 0.52208 | 2187 | 0.5 | 0.3 | 4.691% | 4.691% | default | 0.16 | 1.067
UAE - Techshore - I | 2025-11 | UAE | I | 28 | 125 | JCB 448 (125 kVA) | 2442 | 4031 | 0.60581 | 1.7% | 2972 | 0.73729 | 2939 | 0.5 | 0.3 | 21.7% | 21.7% | default | 0.1 | 1.005
UAE - Techshore - I | 2025-12 | UAE | I | 28 | 125 | JCB 448 (125 kVA) | 2149 | 3061 | 0.70206 | 1.2% | 2593 | 0.84711 | 2560 | 0.5 | 0.3 | 20.66% | 20.66% | default | 0.08 | 1.007
UAE - Techshore - I | 2026-01 | UAE | I | 27 | 125 | JCB 448 (125 kVA) | 1462 | 1611 | 0.90751 | 0.2% | 1793 | 1.113 | 1790 | 0.5 | 0.3 | 22.64% | 22.64% | default | 0.06 | 1.011
UAE - Techshore - I | 2026-02 | UAE | I | 24 | 125 | JCB 448 (125 kVA) | 1429 | 2112 | 0.67661 | 1.4% | 1647 | 0.77983 | 1646 | 0.5 | 0.3 | 15.26% | 15.26% | default | 0.09 | 1.012
UAE - Techshore - I | 2026-03 | UAE | I | 24 | 125 | JCB 448 (125 kVA) | 1309 | 2457 | 0.53276 | 0.9% | 1536 | 0.62515 | 1535 | 0.5 | 0.3 | 17.34% | 17.34% | default | 0.12 | 1.012
UAE - Techshore - I | 2026-04 | UAE | I | 26 | 125 | JCB 448 (125 kVA) | 3414 | 7208 | 0.47364 | 2.1% | 3411 | 0.47322 | 3399 | 0.5 | 0.3 | -0.08787% | 0.08787% | default | 0.19 | 1.25
UAE - Techshore - I | 2026-05 | UAE | I | 29 | 125 | JCB 448 (125 kVA) | 4216 | 9191 | 0.45871 | 5% | 4456 | 0.48482 | 4440 | 0.5 | 0.3 | 5.693% | 5.693% | default | 0.18 | 1.039
UAE - Techshore - I | 2026-06 | UAE | I | 27 | 125 | JCB 448 (125 kVA) | 2301 | 4691 | 0.49051 | 12.8% | 2365 | 0.50416 | 2362 | 0.5 | 0.3 | 2.781% | 2.781% | default | 0.17 | 0.929
UAE - Techshore - I | 2026-07 | UAE | I | 31 | 125 | JCB 448 (125 kVA) | 2459 | 5043 | 0.48761 | 14.8% | 2687 | 0.53282 | 2686 | 0.5 | 0.3 | 9.272% | 9.272% | default | 0.15 | 0.93
UAE - Techshore - I | 2026-08 | UAE | I | 31 | 125 | JCB 448 (125 kVA) | 2582 | 4385 | 0.58883 | 9% | 2365 | 0.53934 | 2364 | 0.5 | 0.3 | -8.404% | 8.404% | default | 0.15 | 0.934
UAE - Techshore - I | 2026-09 | UAE | I | 29 | 125 | JCB 448 (125 kVA) | 2743 | 5212 | 0.52629 | 13.1% | 2460 | 0.47199 | 2460 | 0.5 | 0.3 | -10.32% | 10.32% | default | 0.19 | 1.128
UAE - Trans Asia - I | 2025-01 | UAE | I | 31 | 250 + 60 + 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 6042 | 12509 | 0.48301 | 17.8% | 8059 | 0.64426 | 6243 | 0.5 | 0.3 | 33.38% | 33.38% | default | 0.09 | 1.048
UAE - Trans Asia - I | 2025-02 | UAE | I | 28 | 300 + 60 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 5573 | 11483 | 0.48533 | 22.2% | 7906 | 0.6885 | 5800 | 0.5 | 0.3 | 41.86% | 41.86% | default | 0.08 | 1.143
UAE - Trans Asia - I | 2025-03 | UAE | I | 30 | 300 + 60 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 6298 | 13877 | 0.45384 | 25% | 9074 | 0.65389 | 6623 | 0.5 | 0.3 | 44.08% | 44.08% | default | 0.09 | 1.092
UAE - Trans Asia - I | 2025-04 | UAE | I | 30 | 60 + 300 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 8634 | 23098 | 0.3738 | 20.1% | 9089 | 0.3935 | 8684 | 0.5 | 0.3 | 5.27% | 5.27% | default | 0.22 | 1.126
UAE - Trans Asia - I | 2025-05 | UAE | I | 31 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 10573 | 30544 | 0.34616 | 16% | 11629 | 0.38073 | 11396 | 0.5 | 0.3 | 9.988% | 9.988% | default | 0.23 | 1.011
UAE - Trans Asia - I | 2025-06 | UAE | I | 30 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 9887 | 29712 | 0.33276 | 13.1% | 10818 | 0.3641 | 10195 | 0.5 | 0.3 | 9.416% | 9.416% | default | 0.25 | 0.998
UAE - Trans Asia - I | 2025-07 | UAE | I | 31 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 13487 | 42619 | 0.31646 | 10.9% | 15572 | 0.36538 | 13852 | 0.5 | 0.3 | 15.46% | 15.46% | default | 0.34 | 1.25
UAE - Trans Asia - I | 2025-08 | UAE | I | 31 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 13855 | 44363 | 0.31231 | 9.6% | 16796 | 0.3786 | 14219 | 0.5 | 0.3 | 21.23% | 21.23% | default | 0.35 | 1.25
UAE - Trans Asia - I | 2025-09 | UAE | I | 30 | 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 10939 | 34319 | 0.31874 | 10.9% | 12170 | 0.35461 | 11519 | 0.5 | 0.3 | 11.25% | 11.25% | default | 0.27 | 0.986
UAE - Trans Asia - I | 2025-10 | UAE | I | 31 | 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 10999 | 31112 | 0.35353 | 11.8% | 11082 | 0.3562 | 10514 | 0.5 | 0.3 | 0.7546% | 0.7546% | default | 0.25 | 1.172
UAE - Trans Asia - I | 2025-11 | UAE | I | 30 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 9360 | 25123 | 0.37257 | 11.1% | 9607 | 0.3824 | 9318 | 0.5 | 0.3 | 2.639% | 2.639% | default | 0.25 | 1.142
UAE - Trans Asia - I | 2025-12 | UAE | I | 31 | 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA) | 8423 | 19286 | 0.43674 | 10% | 8076 | 0.41875 | 7936 | 0.5 | 0.3 | -4.12% | 4.12% | default | 0.24 | 1.183
UAE - Trans Asia - I | 2026-01 | UAE | I | 31 | 300 + 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 6622 | 13069 | 0.5067 | 19% | 9857 | 0.75423 | 7312 | 0.5 | 0.3 | 48.85% | 48.85% | default | 0.07 | 0.999
UAE - Trans Asia - I | 2026-02 | UAE | I | 28 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 6484 | 14618 | 0.44356 | 19.6% | 6435 | 0.44021 | 6902 | 0.5 | 0.3 | -0.7557% | 0.7557% | default | 0.25 | 1.007
UAE - Trans Asia - I | 2026-03 | UAE | I | 31 | 60 + 300 | JCB 448 (60 kVA), JD 6090 (300 kVA) | 6599 | 14950 | 0.4414 | 17.1% | 6044 | 0.40428 | 5724 | 0.5 | 0.3 | -8.41% | 8.41% | default | 0.3 | 1.25
UAE - Trans Asia - I | 2026-04 | UAE | I | 30 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 8255 | 20241 | 0.40784 | 19% | 8194 | 0.40482 | 8093 | 0.5 | 0.3 | -0.7389% | 0.7389% | default | 0.27 | 1.117
UAE - Trans Asia - I | 2026-05 | UAE | I | 31 | 60 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 9990 | 27037 | 0.36949 | 15.3% | 11515 | 0.4259 | 10309 | 0.5 | 0.3 | 15.27% | 15.27% | default | 0.26 | 1.04
UAE - Trans Asia - I | 2026-06 | UAE | I | 30 | 300 + 60 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (60 kVA), JD 6090 (300 kVA) | 11786 | 33103 | 0.35604 | 14.1% | 13636 | 0.41193 | 12102 | 0.5 | 0.3 | 15.7% | 15.7% | default | 0.2 | 0.978
UAE - Trans Asia - I | 2026-07 | UAE | I | 31 | 300 + 125 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 12893 | 36162 | 0.35653 | 13% | 14874 | 0.41132 | 13173 | 0.5 | 0.3 | 15.36% | 15.36% | default | 0.2 | 0.927
UAE - Trans Asia - I | 2026-08 | UAE | I | 31 | 125 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 13250 | 37761 | 0.35089 | 12.6% | 13553 | 0.35892 | 12906 | 0.5 | 0.3 | 2.287% | 2.287% | default | 0.29 | 1.046
UAE - Trans Asia - I | 2026-09 | UAE | I | 30 | 125 + 300 + 300 | Cummins QSL9 (250–300 kVA), JCB 448 (125 kVA), JD 6090 (300 kVA) | 13214 | 36635 | 0.36069 | 12.2% | 13585 | 0.37082 | 13318 | 0.5 | 0.3 | 2.808% | 2.808% | default | 0.27 | 0.957
UAE - UG Camp - C | 2025-01 | UAE | C | 23 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 35782 | 122995 | 0.29092 | 19.8% | 38908 | 0.31634 | 38103 | 0.63 | 0.32 | 8.736% | 8.736% | quarter | 0.35 | 1.045
UAE - UG Camp - C | 2025-02 | UAE | C | 25 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 40072 | 132192 | 0.30313 | 24.5% | 40572 | 0.30692 | 39937 | 0.63 | 0.32 | 1.248% | 1.248% | quarter | 0.39 | 1.205
UAE - UG Camp - C | 2025-03 | UAE | C | 31 | 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 44645 | 160072 | 0.27891 | 32% | 49778 | 0.31097 | 48358 | 0.63 | 0.32 | 11.5% | 11.5% | quarter | 0.37 | 0.99
UAE - UG Camp - C | 2025-04 | UAE | C | 30 | 500 + 800 + 1000 + 800 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 67945 | 232474 | 0.29227 | 35% | 69315 | 0.29816 | 68289 | 0.72 | 0.35 | 2.016% | 2.016% | quarter | 0.43 | 1.25
UAE - UG Camp - C | 2025-05 | UAE | C | 28 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 88660 | 311329 | 0.28478 | 32.5% | 90002 | 0.28909 | 89610 | 0.72 | 0.35 | 1.514% | 1.514% | quarter | 0.47 | 1.166
UAE - UG Camp - C | 2025-06 | UAE | C | 29 | 800 + 800 + 500 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 97159 | 344456 | 0.28207 | 29.3% | 99958 | 0.29019 | 99296 | 0.72 | 0.35 | 2.881% | 2.881% | quarter | 0.47 | 1.126
UAE - UG Camp - C | 2025-07 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 126733 | 463126 | 0.27365 | 23.7% | 132345 | 0.28576 | 132357 | 0.76 | 0.39 | 4.428% | 4.428% | quarter | 0.53 | 1.035
UAE - UG Camp - C | 2025-08 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 143756 | 524560 | 0.27405 | 21.4% | 149584 | 0.28516 | 149142 | 0.76 | 0.39 | 4.054% | 4.054% | quarter | 0.55 | 1.25
UAE - UG Camp - C | 2025-09 | UAE | C | 30 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 112056 | 406282 | 0.27581 | 23.7% | 116657 | 0.28713 | 116936 | 0.76 | 0.39 | 4.106% | 4.106% | quarter | 0.53 | 0.967
UAE - UG Camp - C | 2025-10 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 84678 | 301285 | 0.28106 | 27.1% | 87529 | 0.29052 | 88123 | 0.71 | 0.36 | 3.367% | 3.367% | quarter | 0.46 | 1.049
UAE - UG Camp - C | 2025-11 | UAE | C | 30 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 53195 | 185269 | 0.28712 | 27.9% | 55655 | 0.3004 | 56172 | 0.71 | 0.36 | 4.624% | 4.624% | quarter | 0.38 | 1.017
UAE - UG Camp - C | 2025-12 | UAE | C | 31 | 800 + 800 + 500 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 47390 | 158897 | 0.29824 | 22.8% | 48796 | 0.30709 | 49081 | 0.71 | 0.36 | 2.967% | 2.967% | quarter | 0.34 | 1.038
UAE - UG Camp - C | 2026-01 | UAE | C | 31 | 800 + 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 44732 | 155349 | 0.28795 | 19.8% | 48192 | 0.31022 | 47336 | 0.61 | 0.33 | 7.735% | 7.735% | quarter | 0.32 | 1.046
UAE - UG Camp - C | 2026-02 | UAE | C | 28 | 800 + 500 + 800 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 43393 | 153310 | 0.28304 | 24.9% | 47274 | 0.30836 | 46550 | 0.61 | 0.33 | 8.944% | 8.944% | quarter | 0.33 | 1
UAE - UG Camp - C | 2026-03 | UAE | C | 31 | 800 + 800 + 500 + 500 + 1000 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 57623 | 199117 | 0.28939 | 27.7% | 59937 | 0.30101 | 59809 | 0.61 | 0.33 | 4.016% | 4.016% | quarter | 0.36 | 1.045
UAE - UG Camp - C | 2026-04 | UAE | C | 30 | 800 + 500 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 58488 | 203776 | 0.28702 | 31.2% | 61271 | 0.30068 | 60880 | 0.71 | 0.35 | 4.758% | 4.758% | quarter | 0.37 | 0.991
UAE - UG Camp - C | 2026-05 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 89248 | 314034 | 0.2842 | 31.8% | 91265 | 0.29062 | 91037 | 0.71 | 0.35 | 2.26% | 2.26% | quarter | 0.46 | 1.049
UAE - UG Camp - C | 2026-06 | UAE | C | 30 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 98056 | 348371 | 0.28147 | 28.7% | 100571 | 0.28869 | 101099 | 0.71 | 0.35 | 2.565% | 2.565% | quarter | 0.49 | 0.972
UAE - UG Camp - C | 2026-07 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 127674 | 458788 | 0.27829 | 23.4% | 131272 | 0.28613 | 131450 | 0.73 | 0.37 | 2.818% | 2.818% | quarter | 0.52 | 1.007
UAE - UG Camp - C | 2026-08 | UAE | C | 31 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 152470 | 550514 | 0.27696 | 19.2% | 156711 | 0.28466 | 156214 | 0.73 | 0.37 | 2.782% | 2.782% | quarter | 0.52 | 1.124
UAE - UG Camp - C | 2026-09 | UAE | C | 30 | 800 + 800 + 1000 + 500 | Cummins QSK23 (800 kVA), Cummins QST30 (1000 kVA), Volvo TAD1651 (500 kVA) | 123292 | 445710 | 0.27662 | 20.7% | 127399 | 0.28583 | 127285 | 0.73 | 0.37 | 3.331% | 3.331% | quarter | 0.52 | 1.074

## Excluded months
Site | Month | Reason | Days of hourly data | Report DG kWh | Portal DG kWh | Actual L/kWh | Model L/kWh (unreliable)
KSA - ARAMCO PMT - C | 2025-05 | report DG differs >20% from portal | 22 | 216530 | 144646 | 0.353 | 0.334
KSA - ARCC (H) - C | 2025-04 | report DG differs >20% from portal | 21 | 203638 | 128902 | 0.371 | 0.379
KSA - AYTB Harad - C | 2025-01 | part month (<20 days of hourly data) | 2 | 33064 | 2950 | 0.677 | 0.458
KSA - AYTB Harad - C | 2025-04 | report DG differs >20% from portal | 30 | 108769 | 86663 | 0.301 | 0.394
KSA - AYTB Harad - C | 2025-05 | report DG differs >20% from portal | 24 | 137978 | 109842 | 0.365 | 0.398
KSA - AYTB Jubail - C | 2025-01 | part month (<20 days of hourly data) | 11 | 213817 | 183610 | 0.375 | 0.303
KSA - AYTB Jubail - C | 2025-04 | report DG differs >20% from portal | 21 | 381675 | 252460 | 0.357 | 0.326
KSA - Afnan - C | 2025-02 | part month (<20 days of hourly data) | 1 | 46044 | 2674 | 0.422 | 0.401
KSA - Afnan - C | 2025-03 | report DG differs >20% from portal | 31 | 65931 | 53610 | 0.472 | 0.384
KSA - Afnan - C | 2025-04 | report DG differs >20% from portal | 28 | 105616 | 85948 | 0.401 | 0.339
KSA - Afnan - C | 2026-07 | report DG differs >20% from portal | 31 | 14186 | 54194 | 0.314 | 0.51
KSA - Crystal Rabigh - C | 2025-01 | part month (<20 days of hourly data) | 16 | 99430 | 96273 | 0.381 | 0.404
KSA - Crystal Rabigh - C | 2025-04 | report DG differs >20% from portal | 26 | 402888 | 319219 | 0.334 | 0.327
KSA - Crystal Rabigh - C | 2025-08 | part month (<20 days of hourly data) | 13 | 96256 | 90595 | 0.328 | 0.3
KSA - Fame Fardani - C | 2026-04 | part month (<20 days of hourly data) | 8 | 304275 | 101889 | 0.333 | 0.304
KSA - KENT - C | 2025-07 | part month (<20 days of hourly data) | 5 | 479044 | 456096 | 0.286 | 0.322
KSA - KENT - C | 2025-08 | report DG differs >20% from portal | 28 | 496861 | 352658 | 0.309 | 0.323
KSA - KENT - C | 2025-09 | part month (<20 days of hourly data) | 18 | 386202 | 327799 | 0.3 | 0.355
KSA - KENT - C | 2026-01 | part month (<20 days of hourly data) | 3 | 208302 | 155993 | 0.305 | 0.34
KSA - MBL Camp - C | 2026-01 | part month (<20 days of hourly data) | 7 | 6079 | 1720 | 1.25 | 0.582
KSA - MBL Camp - C | 2026-04 | report DG differs >20% from portal | 26 | 13420 | 9635 | 0.451 | 0.467
KSA - MBL JCD Opera - S | 2025-05 | report DG differs >20% from portal | 24 | 38885 | 29547 | 0.453 | 0.425
KSA - MBL JCD Opera - S | 2025-09 | report DG differs >20% from portal | 30 | 45217 | 20255 | 0.436 | 0.433
KSA - MBL Oceanarium - S | 2025-05 | report DG differs >20% from portal | 24 | 16979 | 12992 | 0.486 | 0.459
KSA - MBL Oceanarium - S | 2026-04 | report DG differs >20% from portal | 30 | 16086 | 13194 | 0.428 | 0.46
KSA - MBL Oceanarium - S | 2026-05 | report DG differs >20% from portal | 31 | 15921 | 3545 | 0.43 | 0.469
KSA - MBL Opera - S | 2025-05 | report DG differs >20% from portal | 24 | 21554 | 16375 | 0.425 | 0.399
KSA - MBL Opera - S | 2025-07 | report DG differs >20% from portal | 20 | 25983 | 20583 | 0.427 | 0.375
KSA - MBL Opera - S | 2026-05 | report DG differs >20% from portal | 31 | 16103 | 8347 | 0.481 | 0.449
KSA - MBL Opera - S | 2026-06 | report DG differs >20% from portal | 30 | 18929 | 15035 | 0.42 | 0.417
KSA - Namareq KAEC - C | 2025-04 | part month (<20 days of hourly data) | 6 | 165931 | 95015 | 0.316 | 0.319
KSA - Namareq KAEC - C | 2025-07 | report DG differs >20% from portal | 31 | 798037 | 590585 | 0.339 | 0.309
KSA - Namareq KAEC - C | 2025-08 | report DG differs >20% from portal | 31 | 816141 | 630659 | 0.355 | 0.311
KSA - Namariq Jizan - C | 2025-05 | part month (<20 days of hourly data) | 9 | 831806 | 0 | 0.467 | 0.329
KSA - Namariq Jizan - C | 2025-06 | part month (<20 days of hourly data) | 7 | 1212902 | 0 | 0.366 | 0.316
KSA - Namariq Jizan - C | 2025-07 | part month (<20 days of hourly data) | 16 | 1372019 | 0 | 0.3 | 0.323
KSA - Namariq Jizan - C | 2025-08 | report DG differs >20% from portal | 31 | 1230006 | 600462 | 0.316 | 0.321
KSA - Namariq Jizan - C | 2026-01 | report DG differs >20% from portal | 31 | 646638 | 510824 | 0.332 | 0.33
KSA - Ramz Al Akhwa - C | 2025-07 | part month (<20 days of hourly data) | 14 | 322517 | 331692 | 0.309 | 0.284
KSA - Ramz Al Akhwa - C | 2025-08 | report DG differs >20% from portal | 29 | 387662 | 719133 | 0.294 | 0.282
KSA - Sprint - I | 2025-05 | part month (<20 days of hourly data) | 17 | 14870 | 8007 | 0.478 | 0.466
KSA - Sprint - I | 2025-07 | report DG differs >20% from portal | 31 | 17781 | 22602 | 0.541 | 0.506
KSA - Sprint - I | 2026-08 | report DG differs >20% from portal | 31 | 23423 | 0 | 0.465 | 0.43
KSA - Sprint - I | 2026-09 | report DG differs >20% from portal | 30 | 25448 | 7262 | 0.467 | 0.417
UAE - AL Saida Fujeirah - C | 2025-02 | part month (<20 days of hourly data) | 3 | 17436 | 1412 | 0.534 | 0.481
UAE - AL Saida Fujeirah - C | 2025-04 | report DG differs >20% from portal | 30 | 36000 | 22573 | 0.398 | 0.401
UAE - AL Saida Fujeirah - C | 2025-06 | report DG differs >20% from portal | 22 | 43367 | 30719 | 0.376 | 0.367
UAE - Al Dar - S | 2025-04 | report DG differs >20% from portal | 29 | 35480 | 26516 | 0.391 | 0.494
UAE - Al Dar - S | 2025-05 | report DG differs >20% from portal | 31 | 52703 | 40681 | 0.305 | 0.43
UAE - Al Dar - S | 2025-06 | report DG differs >20% from portal | 30 | 66046 | 52694 | 0.346 | 0.387
UAE - Al Dar - S | 2025-07 | report DG differs >20% from portal | 26 | 91150 | 62016 | 0.346 | 0.343
UAE - Al Dar - S | 2025-08 | report DG differs >20% from portal | 31 | 78787 | 52920 | 0.413 | 0.386
UAE - Al Dar - S | 2026-03 | report DG differs >20% from portal | 31 | 33116 | 20273 | 0.368 | 0.374
UAE - EAST VILLE Fujeirah - C | 2025-04 | report DG differs >20% from portal | 28 | 217442 | 172719 | 0.309 | 0.285
UAE - EAST VILLE Hubshan - C | 2025-04 | report DG differs >20% from portal | 30 | 292809 | 195547 | 0.299 | 0.288
UAE - EAST VILLE Hubshan - C | 2025-05 | report DG differs >20% from portal | 22 | 362914 | 249893 | 0.282 | 0.301
UAE - EAST VILLE Hubshan - C | 2025-06 | report DG differs >20% from portal | 23 | 433032 | 330316 | 0.284 | 0.291
UAE - EAST VILLE Hubshan - C | 2025-10 | report DG differs >20% from portal | 31 | 570135 | 374343 | 0.284 | 0.289
UAE - Galfar - C | 2025-07 | report DG differs >20% from portal | 31 | 666975 | 546322 | 0.285 | 0.271
UAE - Galfar - C | 2026-06 | report DG differs >20% from portal | 30 | 499187 | 410860 | 0.3 | 0.279
UAE - Innovo Build - S | 2025-02 | report DG differs >20% from portal | 25 | 16349 | 11355 | 0.455 | 0.423
UAE - Innovo Build - S | 2025-04 | report DG differs >20% from portal | 26 | 39534 | 30702 | 0.374 | 0.358
UAE - Intermass - S | 2026-02 | report DG differs >20% from portal | 28 | 7613 | 6197 | 0.501 | 0.491
UAE - Intermass - S | 2026-03 | report DG differs >20% from portal | 30 | 5664 | 3831 | 0.622 | 0.521
UAE - Intermass - S | 2026-09 | part month (<20 days of hourly data) | 2 | 1151 | 699 | 0.294 | 0.393
UAE - KITOPI Alqouz- I | 2025-03 | report DG differs >20% from portal | 23 | 35683 | 29369 | 0.398 | 0.426
UAE - MNH Fujairah - C | 2026-06 | part month (<20 days of hourly data) | 7 | 47798 | 38615 | 0.291 | 0.304
UAE - Natural Fragrances - I | 2025-01 | part month (<20 days of hourly data) | 16 | 8946 | 6789 | 0.45 | 0.496
UAE - Natural Fragrances - I | 2025-02 | report DG differs >20% from portal | 25 | 8965 | 6076 | 0.435 | 0.429
UAE - Natural Fragrances - I | 2025-03 | report DG differs >20% from portal | 27 | 8555 | 6108 | 0.382 | 0.389
UAE - Natural Fragrances - I | 2025-08 | report DG differs >20% from portal | 31 | 31099 | 25628 | 0.319 | 0.309
UAE - Natural Fragrances - I | 2025-11 | report DG differs >20% from portal | 30 | 17196 | 14192 | 0.384 | 0.358
UAE - Natural Fragrances - I | 2026-02 | part month (<20 days of hourly data) | 15 | 4940 | 4252 | 0.625 | 0.442
UAE - Nordic - I | 2025-06 | report DG differs >20% from portal | 22 | 120819 | 93713 | 0.314 | 0.297
UAE - Nordic - I | 2026-03 | report DG differs >20% from portal | 31 | 124647 | 98888 | 0.333 | 0.31
UAE - SJ ABED - C | 2025-07 | part month (<20 days of hourly data) | 1 | 3289 | 794 | 0.618 | 0.346
UAE - SJ ABED - C | 2025-08 | report DG differs >20% from portal | 31 | 148564 | 119434 | 0.3 | 0.324
UAE - Seven Brothers - C | 2025-12 | part month (<20 days of hourly data) | 17 | 24809 | 9510 | 0.525 | 0.451
UAE - Seven Brothers - C | 2026-08 | report DG differs >20% from portal | 31 | 244406 | 196802 | 0.287 | 0.299
UAE - Specialist - C | 2025-05 | report DG differs >20% from portal | 25 | 86186 | 64567 | 0.397 | 0.347
UAE - Target - C | 2025-03 | part month (<20 days of hourly data) | 15 | 310564 | 129447 | 0.309 | 0.308
UAE - Techshore - I | 2025-01 | part month (<20 days of hourly data) | 19 | 2643 | 2481 | 0.746 | 0.846

## Site summary
Site | Months | From | To | Actual fuel (L) | Actual L/kWh | Model fuel (L) | Model L/kWh | Whole-period error | Typical monthly ¦error¦ | Dispatch-only error (model vs curves on actual running)
KSA - ARAMCO PMT - C | 20 | 2025-01 | 2026-09 | 1119572 | 0.33658 | 1121744 | 0.33723 | 0.194% | 4.5% | -1.019%
KSA - ARCC (H) - C | 13 | 2025-01 | 2026-02 | 946297 | 0.35982 | 941479 | 0.35799 | -0.5091% | 5.11% | 3.254%
KSA - AYTB Harad - C | 9 | 2025-02 | 2025-12 | 323234 | 0.35332 | 321262 | 0.35116 | -0.6101% | 12.48% | 5.319%
KSA - AYTB Jubail - C | 19 | 2025-02 | 2026-09 | 2355267 | 0.31678 | 2420389 | 0.32554 | 2.765% | 5.14% | 2.953%
KSA - Afnan - C | 14 | 2025-05 | 2026-06 | 569292 | 0.33631 | 571436 | 0.33758 | 0.3766% | 5.46% | -0.3036%
KSA - Crystal Rabigh - C | 5 | 2025-02 | 2025-07 | 537936 | 0.33552 | 507671 | 0.31664 | -5.626% | 4.97% | 1.222%
KSA - Fame Fardani - C | 5 | 2026-05 | 2026-09 | 1093909 | 0.30148 | 1116931 | 0.30783 | 2.105% | 2.03% | 0.588%
KSA - Formula Arabia - C | 10 | 2025-12 | 2026-09 | 631455 | 0.33813 | 624303 | 0.3343 | -1.133% | 2.18% | -0.737%
KSA - KENT - C | 8 | 2026-02 | 2026-09 | 744631 | 0.27788 | 876090 | 0.32694 | 17.65% | 18.15% | -0.4544%
KSA - MBL Camp - C | 7 | 2026-02 | 2026-09 | 139744 | 0.45289 | 149021 | 0.48296 | 6.639% | 15.27% | 4.33%
KSA - MBL JCD Opera - S | 19 | 2025-01 | 2026-09 | 381852 | 0.49976 | 352375 | 0.46118 | -7.719% | 8.67% | -6.327%
KSA - MBL Oceanarium - S | 18 | 2025-01 | 2026-09 | 156131 | 0.46815 | 156960 | 0.47064 | 0.531% | 7.76% | -0.3435%
KSA - MBL Opera - S | 17 | 2025-01 | 2026-09 | 152505 | 0.45694 | 136967 | 0.41039 | -10.19% | 8.25% | -0.4622%
KSA - Namareq KAEC - C | 15 | 2025-05 | 2026-09 | 2406769 | 0.33554 | 2272463 | 0.31682 | -5.58% | 3.27% | -1.008%
KSA - Namariq Jizan - C | 12 | 2025-09 | 2026-09 | 3771083 | 0.30712 | 3898880 | 0.31753 | 3.389% | 5.11% | -0.8269%
KSA - Ramz Al Akhwa - C | 13 | 2025-09 | 2026-09 | 508322 | 0.31491 | 521623 | 0.32315 | 2.617% | 4.66% | 0.6841%
KSA - Sprint - I | 17 | 2025-01 | 2026-07 | 104167 | 0.63497 | 91594 | 0.55833 | -12.07% | 17.9% | -0.07528%
UAE - AL Saida Fujeirah - C | 2 | 2025-03 | 2025-05 | 24987 | 0.38136 | 24810 | 0.37866 | -0.7084% | 7.89% | -3.553%
UAE - Al Dar - S | 15 | 2025-01 | 2026-09 | 281820 | 0.37437 | 299849 | 0.39832 | 6.397% | 11.67% | 1.791%
UAE - Arabian Industries - C | 17 | 2025-05 | 2026-09 | 486298 | 0.31998 | 486766 | 0.32029 | 0.09624% | 7.98% | -0.5258%
UAE - EAST VILLE Fujeirah - C | 20 | 2025-01 | 2026-09 | 1476040 | 0.29947 | 1411993 | 0.28648 | -4.339% | 4.88% | 0.6132%
UAE - EAST VILLE Hubshan - C | 17 | 2025-01 | 2026-09 | 2358495 | 0.28212 | 2427369 | 0.29036 | 2.92% | 2.97% | 0.02308%
UAE - ENATA - I | 1 | 2025-01 | 2025-01 | 21372 | 0.45488 | 18996 | 0.40431 | -11.12% | 11.12% | -7.611%
UAE - Galfar - C | 17 | 2025-03 | 2026-09 | 2148146 | 0.29019 | 2049672 | 0.27688 | -4.584% | 3.54% | -0.315%
UAE - Innovo Build - S | 16 | 2025-01 | 2026-06 | 205461 | 0.3845 | 192035 | 0.35937 | -6.535% | 5.92% | 1.974%
UAE - Intermass - S | 18 | 2025-01 | 2026-08 | 149930 | 0.44882 | 144313 | 0.43201 | -3.746% | 10.1% | 0.7695%
UAE - KITOPI Alqouz- I | 20 | 2025-01 | 2026-09 | 324085 | 0.35605 | 368189 | 0.4045 | 13.61% | 11.91% | 6.363%
UAE - MNH Fujairah - C | 3 | 2026-07 | 2026-09 | 197542 | 0.29554 | 204594 | 0.30609 | 3.57% | 3.18% | 0.4128%
UAE - Natural Fragrances - I | 8 | 2025-04 | 2026-01 | 55645 | 0.34264 | 54822 | 0.33758 | -1.479% | 2.93% | 0.08946%
UAE - Nordic - I | 19 | 2025-01 | 2026-09 | 762004 | 0.3188 | 736360 | 0.30807 | -3.365% | 6.38% | -2.07%
UAE - SJ ABED - C | 13 | 2025-09 | 2026-09 | 413020 | 0.33314 | 423498 | 0.34159 | 2.537% | 4.52% | 2.53%
UAE - Seven Brothers - C | 8 | 2026-01 | 2026-09 | 179361 | 0.33431 | 177409 | 0.33067 | -1.088% | 6.85% | -3.722%
UAE - Specialist - C | 16 | 2025-06 | 2026-09 | 474440 | 0.3436 | 452820 | 0.32794 | -4.557% | 4.6% | 1.092%
UAE - Target - C | 18 | 2025-04 | 2026-09 | 3439271 | 0.28676 | 3585076 | 0.29892 | 4.239% | 4.57% | 0.1287%
UAE - Techshore - I | 20 | 2025-02 | 2026-09 | 45712 | 0.52458 | 48917 | 0.56136 | 7.011% | 9.58% | 0.2069%
UAE - Trans Asia - I | 21 | 2025-01 | 2026-09 | 203164 | 0.3683 | 227570 | 0.41255 | 12.01% | 9.99% | 10.4%
UAE - UG Camp - C | 21 | 2025-01 | 2026-09 | 1737049 | 0.28144 | 1802994 | 0.29213 | 3.796% | 3.37% | 0.33%

## Fleet by month
Month | Sites | Actual fuel (L) | Actual DG kWh | Actual L/kWh | Model fuel (L) | Model L/kWh | Fleet error
2025-01 | 16 | 341288 | 877354 | 0.389 | 332395 | 0.37886 | -2.606%
2025-02 | 18 | 447147 | 1159654 | 0.38559 | 423700 | 0.36537 | -5.244%
2025-03 | 20 | 611082 | 1823736 | 0.33507 | 619448 | 0.33966 | 1.369%
2025-04 | 14 | 571930 | 1856913 | 0.308 | 581766 | 0.3133 | 1.72%
2025-05 | 18 | 1436423 | 4435092 | 0.32388 | 1371372 | 0.30921 | -4.529%
2025-06 | 23 | 1726352 | 5393469 | 0.32008 | 1674459 | 0.31046 | -3.006%
2025-07 | 21 | 1653154 | 5380815 | 0.30723 | 1639479 | 0.30469 | -0.8272%
2025-08 | 22 | 1835398 | 6218568 | 0.29515 | 1869079 | 0.30056 | 1.835%
2025-09 | 27 | 2106302 | 6934625 | 0.30374 | 2118633 | 0.30552 | 0.5854%
2025-10 | 27 | 1495534 | 4739478 | 0.31555 | 1504769 | 0.3175 | 0.6175%
2025-11 | 27 | 1208282 | 3670586 | 0.32918 | 1189829 | 0.32415 | -1.527%
2025-12 | 29 | 1076540 | 3217438 | 0.3346 | 1067713 | 0.33185 | -0.8199%
2026-01 | 28 | 786522 | 2347501 | 0.33505 | 801184 | 0.34129 | 1.864%
2026-02 | 29 | 1055363 | 3226841 | 0.32706 | 1071533 | 0.33207 | 1.532%
2026-03 | 26 | 1141151 | 3603528 | 0.31668 | 1189236 | 0.33002 | 4.214%
2026-04 | 27 | 1309272 | 4139561 | 0.31628 | 1350542 | 0.32625 | 3.152%
2026-05 | 28 | 1933081 | 6288852 | 0.30738 | 1985839 | 0.31577 | 2.729%
2026-06 | 28 | 1970713 | 6463658 | 0.30489 | 2038882 | 0.31544 | 3.459%
2026-07 | 29 | 2489215 | 8153838 | 0.30528 | 2543153 | 0.3119 | 2.167%
2026-08 | 27 | 2958391 | 9766621 | 0.30291 | 3038509 | 0.31111 | 2.708%
2026-09 | 27 | 2772867 | 9086474 | 0.30516 | 2807720 | 0.309 | 1.257%